## Legend for Data Fields
Legend for Data Fields
ID | This is a sequential numeric identifier; you can put any number you want -- I'll have to overwrite it eventually anyway
Attachment | TRUE if there's a file attached to this entry; FALSE if not
Title | A brief title for the item
Discipline | Enter one or more disciplines separated by a semicolon. Valid entries include Civil, Electrical, I&C, Mechanical, and Admin
System/Topic | A system or topic to identify the item; try to keep less than about 5 words
Department | Valid entries include Design, Startup, Construction, Project Control, etc.
APEX Category | Enter one or more categories separated by a semicolon. Valid entries include Safety, Quality, Schedule Performance, and Cost Savings
Description | Describe what the issue or problem is in more detail
Resolution | Describe what the fix or resolution is in more detail
Approval Status | Make every entry in this column Pending
legacy_LL_submitter | Leave blank
legacy_LL_created_date | Leave blank
legacy_LL_approved_date | Leave blank
Checklist Display | TRUE if this entry should appear in your discipline's Design For Safety cheklist; FALSE if not
Created By | Leave blank
Modified By | Leave blank

## Prevention through Design
ID | Title | Engineering Discipline | System/Topic | Department | Entry Category | Description | Resolution | Point of Contact
137 | Hazardous Substances | Civil; Mechanical; Electrical; I&C | Contract Drawings | Design | Safety | Hazardous and toxic substances existing on the project site can create safety and health hazards during construction. | Research the history of the project site and alert the constructor of the type and location of any hazardous and toxic substances existing on the site. All engineering disciplines should provide input into a drawing showing all undergrounds. | Alan Speegle (Southern Co.)
138 | Access Doors | Civil | Architectural | Design | Safety | Access doors in floors and roofs present fall hazards when no guardrails are used around the doors when they are opened. | Use access doors which automatically provide a guarded opening when the doors are opened. | Alan Speegle (Southern Co.)
139 | Doors | Civil | Architectural | Design | Safety | Doors which open into passageways and work areas can strike other workers, and also limit the width of the passage or work area when open. | For access doors through floors, use doors which immediately provide guarded entry around the hole perimeter when the door is opened. | Alan Speegle (Southern Co.)
140 | Doors | Civil | Architectural | Design | Safety | Doors which open into passageways and work areas can strike other workers, and also limit the width of the passage or work area when open. | Design doors to swing away from passageways and platforms when opened. | Alan Speegle (Southern Co.)
141 | Doors | Civil | Architectural | Design | Safety | Doors which open into passageways and work areas can strike other workers, and also limit the width of the passage or work area when open. | Design doors to swing open in the direction of exit travel. | Alan Speegle (Southern Co.)
142 | Doors | Civil | Architectural | Design | Safety | Doors which open into passageways and work areas can strike other workers, and also limit the width of the passage or work area when open. | Design and schedule doors to be installed late in the construction phase. | Alan Speegle (Southern Co.)
143 | Doors | Civil | Architectural | Design | Safety | Doors which open into passageways and work areas can strike other workers, and also limit the width of the passage or work area when open. | Select door hardware that can keep doors in an open position without props or blocking. | Alan Speegle (Southern Co.)
144 | Doors | Civil | Architectural | Design | Safety | Doors which open into passageways and work areas can strike other workers, and also limit the width of the passage or work area when open. | Design and schedule new fire doors to be hung as early as possible in the construction phase. In demolition projects, keep existing fire doors in place as long as possible. | Alan Speegle (Southern Co.)
145 | Doors | Civil | Architectural | Design | Safety | Doors which open into passageways and work areas can strike other workers, and also limit the width of the passage or work area when open. | Provide door protection such that natural elements (snow, wind, lightning) will not cause unsafe conditions. | Alan Speegle (Southern Co.)
146 | Windows | Civil | Architectural | Design | Safety | Prior to installation of upper story windows, low sill heights add to the chance of falling through the window openings. | Design window sills to be 42 inches minimum above the floor level. Window sills at this height will act as guard rails during construction. | Alan Speegle (Southern Co.)
147 | Windows | Civil | Architectural | Design | Safety | Prior to installation of upper story windows, low sill heights add to the chance of falling through the window openings. | Design window sills at a consistant level throughout the project | Alan Speegle (Southern Co.)
148 | Siding | Civil | Architectural | Design | Safety | Try to engineer, procure and install without any scope changes. | Locate wall and roof penetrations early. This will require coordinate with other disciplines, | Alan Speegle (Southern Co.)
149 | Siding | Civil | Architectural | Design | Safety | Try to engineer, procure and install without any scope changes. | Coordinate with mechanical person doing HVAC louvers and dampers. | Alan Speegle (Southern Co.)
150 | Siding | Civil | Architectural | Design | Safety | Try to engineer, procure and install without any scope changes. | Identify on the drawings where siding will be left out for equipment installation or construction access. | Alan Speegle (Southern Co.)
151 | Siding | Civil | Architectural | Design | Safety | Try to engineer, procure and install without any scope changes. | Coordinate shelf angles for fire-rated siding assemblies. | Alan Speegle (Southern Co.)
152 | Siding | Civil | Architectural | Design | Safety | Try to engineer, procure and install without any scope changes. | Consider long spanning siding systems to reduce girt requirements. | Alan Speegle (Southern Co.)
153 | Siding | Civil | Architectural | Design | Safety | Try to engineer, procure and install without any scope changes. | Consider specifying light gauge framing for openings in siding so that they can be framed by siding contractors. | Alan Speegle (Southern Co.)
154 | Siding | Civil | Architectural | Design | Safety | Try to engineer, procure and install without any scope changes. | Specify the proper end flashing to direct water outside of the building. | Alan Speegle (Southern Co.)
155 | Siding | Civil | Architectural | Design | Safety | Try to engineer, procure and install without any scope changes. | Consider specifing that the siding contractor will provide boot flashing in siding openings. | Alan Speegle (Southern Co.)
156 | Siding | Civil | Architectural | Design | Safety | Try to engineer, procure and install without any scope changes. | Seal the top edge to prevent moisture infiltrations and and condensation. | Alan Speegle (Southern Co.)
157 | Siding | Civil | Architectural | Design | Safety | Try to engineer, procure and install without any scope changes. | Locate roof-to-wall curb transitions such that condensate from siding and water run-off are directed to the outside of the building. | Alan Speegle (Southern Co.)
158 | Siding | Civil | Architectural | Design | Safety | Try to engineer, procure and install without any scope changes. | Specify the siding contractor will furnish and install expand-o-flash materials for roof to wall transitions. | Alan Speegle (Southern Co.)
159 | Siding | Civil | Architectural | Design | Safety | Try to engineer, procure and install without any scope changes. | Evaluate with the project team and plant representative the advantages and disadvantages of steel and aluminum application areas. | Alan Speegle (Southern Co.)
160 | Siding | Civil | Architectural | Design | Safety | Try to engineer, procure and install without any scope changes. | Drawing detail should show at least 1/2 inch between bottom edge of siding and the flashing. | Alan Speegle (Southern Co.)
161 | Siding | Civil | Architectural | Design | Safety | Try to engineer, procure and install without any scope changes. | Bar extension on girts for door openings are only needed on the hing side of doors with full and half surface hinges. | Alan Speegle (Southern Co.)
162 | Siding | Civil | Architectural | Design | Safety | Try to engineer, procure and install without any scope changes. | Bar extensions on girts for framed openings is only required for the sills. | Alan Speegle (Southern Co.)
163 | Code | Civil | Architectural | Design | Safety | Determine code requirements during the scoping and conceptual phase of the project. | Determine Americians With Disability (ADA) access requirements with the plant representative. | Alan Speegle (Southern Co.)
164 | Code | Civil | Architectural | Design | Safety | Determine code requirements during the scoping and conceptual phase of the project. | Determine building code classification with the building officials as early as possible before construction starts. | Alan Speegle (Southern Co.)
165 | Code | Civil | Architectural | Design | Safety | Determine code requirements during the scoping and conceptual phase of the project. | Determine building code requirments and insurance carrier requirements for fire wall and other rated areas. | Alan Speegle (Southern Co.)
166 | Code | Civil | Architectural | Design | Safety | Determine code requirements during the scoping and conceptual phase of the project. | Discuss with construction services who is responsible for sealing siding openings, especially in environmentally controlled rooms and rack rooms. Concrete block is not the best option. | Alan Speegle (Southern Co.)
167 | Excavations | Civil | Sitework | Design | Safety | Excavations can present cave-in hazards for construction workers. | Consider using a pile or caisson foundation system which does not require excessively deep excavations and allows construction work to be performed above grade. | Alan Speegle (Southern Co.)
168 | Excavations | Civil | Sitework | Design | Safety | Excavations can present cave-in hazards for construction workers. | Minimize the amount of excavation work and maintain a constant foundation depth throughout the project. | Alan Speegle (Southern Co.)
169 | Excavations | Civil | Sitework | Design | Safety | Excavations can present cave-in hazards for construction workers. | Design and schedule the project to minimize the amount of time excavations are open. | Alan Speegle (Southern Co.)
170 | Excavations | Civil | Sitework | Design | Safety | Excavations can present cave-in hazards for construction workers. | Keep detailed work above grade; simplify all below grade work. | Alan Speegle (Southern Co.)
171 | Excavations | Civil | Sitework | Design | Safety | Excavations can present cave-in hazards for construction workers. | Allow adequate clearance for shoring, forms, and workers within the excavation. | Alan Speegle (Southern Co.)
172 | Excavations | Civil | Sitework | Design | Safety | Excavations can present cave-in hazards for construction workers. | Minimize the amount of excavations required in backfilled or other loose soil, and where there are vibrations from railroads, highway traffic, or large machines. | Alan Speegle (Southern Co.)
173 | Excavations | Civil | Sitework | Design | Safety | Excavations can present cave-in hazards for construction workers. | Provide road access into large, deep excavations such as wastewater treatment ponds or bath tub shaped excavations. | Alan Speegle (Southern Co.)
174 | Excavations | Civil | Sitework | Design | Safety | Excavations can present cave-in hazards for construction workers. | Provide a seal slab or walls in excavations where the soil is saturated or likely to flood the excavation before backfilling. | Alan Speegle (Southern Co.)
175 | Excavations | Civil | Sitework | Design | Safety | Excavations can present cave-in hazards for construction workers. | When possible, avoid excavations below the water table. | Alan Speegle (Southern Co.)
176 | Excavations | Civil | Sitework | Design | Safety | Excavations can present cave-in hazards for construction workers. | When possible, avoid the use of sheet piling. | Alan Speegle (Southern Co.)
177 | Excavations | Civil | Sitework | Design | Safety | Excavations can present cave-in hazards for construction workers. | Comply with CAL OSHA shoring requirements of excavaton during foundation and underground utility designs. Try to avoid deep footings and trenches. | Alan Speegle (Southern Co.)
178 | Excavations | Civil | Sitework | Design | Safety | Excavations can present cave-in hazards for construction workers. | Consider specifing fabric or granular material or mud mats in the bottom of excavations. | Alan Speegle (Southern Co.)
179 | Trenches | Civil | Sitework | Design | Safety | Trench excavation for underground utilities can lead to cave-in hazards for construction workers. | Allow for the placement of underground utilities using trenchless technologies rather than the cut and cover method. | Alan Speegle (Southern Co.)
180 | Trenches | Civil | Sitework | Design | Safety | Trench excavation for underground utilities can lead to cave-in hazards for construction workers. | Avoid requiring trenches in previously backfilled or disturbed soil, or which cross between different types or conditions of soil. | Alan Speegle (Southern Co.)
181 | Trenches | Civil | Sitework | Design | Safety | Trench excavation for underground utilities can lead to cave-in hazards for construction workers. | Avoid designing utilities which cross under existing pipelines, run parallel to immediately adjacent existing pipelines, or intersect manhole excavations. | Alan Speegle (Southern Co.)
182 | Storm Sewers | Civil | Sitework | Design | Safety | Inadequate sewer coverings and bypasses can create safety hazards for construction workers. | Design open drainage pipes for storm sewers to allow for easy access to and removal of debris. | Alan Speegle (Southern Co.)
183 | Storm Sewers | Civil | Sitework | Design | Safety | Inadequate sewer coverings and bypasses can create safety hazards for construction workers. | Design sewer gratings such that the openings are not easily plugged by debris, but not too large that a worker's foot will go through. | Alan Speegle (Southern Co.)
184 | Storm Sewers | Civil | Sitework | Design | Safety | Inadequate sewer coverings and bypasses can create safety hazards for construction workers. | Cover open drainage routes in high foot traffic areas to prevent tripping hazards. | Alan Speegle (Southern Co.)
185 | Storm Sewers | Civil | Sitework | Design | Safety | Inadequate sewer coverings and bypasses can create safety hazards for construction workers. | Design all impoundments or holding ponds with emergency bypass capabilities. | Alan Speegle (Southern Co.)
186 | Storm Sewers | Civil | Sitework | Design | Safety | Inadequate sewer coverings and bypasses can create safety hazards for construction workers. | Ensure that all accessways and manholes are provided with venting or non-venting lids appropriate to the service and traffic location. | Alan Speegle (Southern Co.)
187 | Storm Sewers | Civil | Sitework | Design | Safety | Inadequate sewer coverings and bypasses can create safety hazards for construction workers. | Specify corrugated HPDE pipe for storm drains. | Alan Speegle (Southern Co.)
188 | Process Sewers | Civil | Sitework | Design | Safety | Sewer systems which are not designed for the surrounding conditions and the liquids they will carry can be safety hazards for construction workers. | Ensure that all open sewer embankments are designed for adequate stability under anticipated worksite conditions. | Alan Speegle (Southern Co.)
189 | Process Sewers | Civil | Sitework | Design | Safety | Sewer systems which are not designed for the surrounding conditions and the liquids they will carry can be safety hazards for construction workers. | Provide sewers with adequate accessways to allow for inspection and maintenance operations. | Alan Speegle (Southern Co.)
190 | Process Sewers | Civil | Sitework | Design | Safety | Sewer systems which are not designed for the surrounding conditions and the liquids they will carry can be safety hazards for construction workers. | Ensure that sewer lines are suitable for the maximum temperature service conditions. | Alan Speegle (Southern Co.)
191 | Process Sewers | Civil | Sitework | Design | Safety | Sewer systems which are not designed for the surrounding conditions and the liquids they will carry can be safety hazards for construction workers. | Provide adequate clearance between process/sanitary sewers and any adjacent or crossing potable water lines. | Alan Speegle (Southern Co.)
192 | Process Sewers | Civil | Sitework | Design | Safety | Sewer systems which are not designed for the surrounding conditions and the liquids they will carry can be safety hazards for construction workers. | Design process/effluent sewer systems to vent any gases to the outside of all buildings or other project work areas. | Alan Speegle (Southern Co.)
193 | Underground Utilities | Civil | Sitework | Design | Safety | Existing underground utilities create safety hazards for construction workers during excavation and installation of piles or caissons. | Require the constructor to locate, or "pothole", existing underground utilities before excavation operations begin. | Alan Speegle (Southern Co.)
194 | Underground Utilities | Civil | Sitework | Design | Safety | Existing underground utilities create safety hazards for construction workers during excavation and installation of piles or caissons. | Require hand excavation when near existing underground utilities. | Alan Speegle (Southern Co.)
195 | Underground Utilities | Civil | Sitework | Design | Safety | Existing underground utilities create safety hazards for construction workers during excavation and installation of piles or caissons. | Design underground utiltiies (piping, ductwork, storm drains and etc) early enough so that they can be installed during the site work and foundation phase of the project. | Alan Speegle (Southern Co.)
196 | Underground Utilities | Civil | Sitework | Design | Safety | Existing underground utilities create safety hazards for construction workers during excavation and installation of piles or caissons. | Engineering representatives should coordinate the underground lines so they can be in common trenches and installed at the same time. | Alan Speegle (Southern Co.)
197 | Underground Utilities | Civil | Sitework | Design | Safety | Existing underground utilities create safety hazards for construction workers during excavation and installation of piles or caissons. | Consider making a composite drawing of all existing and proposed under ground utilities. This provide a good planning drawing and reduces the possibility of interferences. | Alan Speegle (Southern Co.)
198 | Slopes | Civil | Sitework | Design | Safety | Project sites which contain steep slopes and limited sight distances can lead to safety hazards for construction workers. | Orient the project layout or grade the site accordingly to minimize the amount of work on steep slopes. | Alan Speegle (Southern Co.)
199 | Slopes | Civil | Sitework | Design | Safety | Project sites which contain steep slopes and limited sight distances can lead to safety hazards for construction workers. | Maintain site distances on the project site and haul roads. | Alan Speegle (Southern Co.)
200 | Slopes | Civil | Sitework | Design | Safety | Project sites which contain steep slopes and limited sight distances can lead to safety hazards for construction workers. | Limit long hauls on steep grades. | Alan Speegle (Southern Co.)
201 | Slopes | Civil | Sitework | Design | Safety | Project sites which contain steep slopes and limited sight distances can lead to safety hazards for construction workers. | Prepare, or require the submittal of, an erosion control plan. | Alan Speegle (Southern Co.)
202 | Sidewalk | Civil | Sitework | Design | Safety | Exterior walkways and other flatwork can lead to tripping and slipping hazards for construction workers. | Consider providing a covering over walkways to protect them from cooling tower plume. | Alan Speegle (Southern Co.)
203 | Sidewalk | Civil | Sitework | Design | Safety | Exterior walkways and other flatwork can lead to tripping and slipping hazards for construction workers. | Design a minimum amount of slope into walkways to prevent puddling. | Alan Speegle (Southern Co.)
204 | General | Electrical | Electrical | Design | Safety | Electrical: General | Project Engineer has communicated “HASCOM” project information required for design engineering personnel making site visits. (Each person that is sent to the job site must be informed of any potential hazards.) | Alan Speegle (Southern Co.)
205 | General | Electrical | Electrical | Design | Safety | Electrical: General | A constructability meeting has been held with representatives from Plant, Construction Services, and Power Engineering to discuss safety-related items. | Alan Speegle (Southern Co.)
206 | General | Electrical | Electrical | Design | Safety | Electrical: General | Underground hazards (electrical duct banks and cables, buried pipes, etc.) and reference drawings locating any potential hazards are identified. | Alan Speegle (Southern Co.)
207 | General | Electrical | Electrical | Design | Safety | Electrical: General | Prohibit access near hoist and crane electrification components. | Alan Speegle (Southern Co.)
208 | General | Electrical | Electrical | Design | Safety | Electrical: General | Applicable codes and standards have been reviewed for requirements impacting the design of a safe facility. | Alan Speegle (Southern Co.)
209 | General | Electrical | Electrical | Design | Safety | Electrical: General | All potentially hazardous areas have been defined per Chapter 5 of the National Electrical Code. Hazardous areas have been identified and boundaries located. | Alan Speegle (Southern Co.)
210 | Equipment | Electrical | Electrical | Design | Safety | Electrical: Equipment | Equipment and electrical devices located in hazardous areas meet requirements for area classification. | Alan Speegle (Southern Co.)
211 | Equipment | Electrical | Electrical | Design | Safety | Electrical: Equipment | Provide electrical system enclosures which are adequate for the expected environmental and climate conditions. | Alan Speegle (Southern Co.)
212 | Equipment | Electrical | Electrical | Design | Safety | Electrical: Equipment | Equipment is located for easy access and operation from floor level. | Alan Speegle (Southern Co.)
213 | Equipment | Electrical | Electrical | Design | Safety | Electrical: Equipment | Do not locate electrical rooms under pipes carrying liquids. | Alan Speegle (Southern Co.)
214 | Equipment | Electrical | Electrical | Design | Safety | Electrical: Equipment | Electrical equipment has been located to maintain proper safety and working maintenance clearances. | Alan Speegle (Southern Co.)
215 | Equipment | Electrical | Electrical | Design | Safety | Electrical: Equipment | Access ways are clear of any electrical equipment that might cause ingress or egress obstruction. Position controls and control panels away from passageways and work areas. | Alan Speegle (Southern Co.)
216 | Equipment | Electrical | Electrical | Design | Safety | Electrical: Equipment | Exit door for emergency egress are properly located in switchgear and high voltage rooms. | Alan Speegle (Southern Co.)
217 | Equipment | Electrical | Electrical | Design | Safety | Electrical: Equipment | Emergency controls and displays are clearly identified. Provide safety switches, pull cords, alarms, etc. which are standardized, clearly displayed, and easily identifiable. | Alan Speegle (Southern Co.)
218 | Equipment | Electrical | Electrical | Design | Safety | Electrical: Equipment | Ensure a disconnect means is provided for all sources of power supply to the equipment. For electrical power there must be an air gap between the line and/or equipment and all sources of power. | Alan Speegle (Southern Co.)
219 | Equipment | Electrical | Electrical | Design | Safety | Electrical: Equipment | Warning devices (e.g., fire alarms, smoke alarms, sirens, etc.) are standardized and different systems are compatible with each other. | Alan Speegle (Southern Co.)
220 | Grounding and Lightning Protection | Electrical | Electrical | Design | Safety | Electrical: Grounding and Lightning Protection | All electrical equipment, major mechanical equipment (i.e., pumps, valves, piping systems, etc.) and civil/structural components (i.e., columns, rebar, handrails, etc.) are properly grounded. | Alan Speegle (Southern Co.)
221 | Grounding and Lightning Protection | Electrical | Electrical | Design | Safety | Electrical: Grounding and Lightning Protection | Cable tray systems are adequately and properly grounded. | Alan Speegle (Southern Co.)
222 | Grounding and Lightning Protection | Electrical | Electrical | Design | Safety | Electrical: Grounding and Lightning Protection | Conduits that are used as ground paths are continuous and securely installed. | Alan Speegle (Southern Co.)
223 | Grounding and Lightning Protection | Electrical | Electrical | Design | Safety | Electrical: Grounding and Lightning Protection | Equipment grounding circuits run to all motors, lighting fixtures, and transformers rated 480 volt or above. | Alan Speegle (Southern Co.)
224 | Grounding and Lightning Protection | Electrical | Electrical | Design | Safety | Electrical: Grounding and Lightning Protection | Lightning protection is adequate for all buildings and structures. | Alan Speegle (Southern Co.)
225 | Grounding and Lightning Protection | Electrical | Electrical | Design | Safety | Electrical: Grounding and Lightning Protection | Lightning protection conforms to the requirements of National Fire Protection Association (NFPA) Standard No. 780 and Southern Generation "Standard for the Design and Installation of Lightning Protection Systems for Generation Facilities". | Alan Speegle (Southern Co.)
226 | Raceways | Electrical | Electrical | Design | Safety | Electrical: Raceways | Input from Civil Design has been obtained for raceway supports where necessary. | Alan Speegle (Southern Co.)
227 | Raceways | Electrical | Electrical | Design | Safety | Electrical: Raceways | Fire stops have been included for all cable tray and conduit penetrations of fire-rated walls or floors. | Alan Speegle (Southern Co.)
228 | Raceways | Electrical | Electrical | Design | Safety | Electrical: Raceways | Fire stops have been included for cable tray vertical risers at all floors. | Alan Speegle (Southern Co.)
229 | Raceways | Electrical | Electrical | Design | Safety | Electrical: Raceways | Cable trays are marked to show the voltage level of the contained circuits (i.e., instrument, 120 volt control, 480 volt power, 4160 volt power, etc.). | Alan Speegle (Southern Co.)
230 | Raceways | Electrical | Electrical | Design | Safety | Electrical: Raceways | Cable tray covers are specified at floor transitions and where cable is exposed to possible damage. | Alan Speegle (Southern Co.)
231 | Raceways | Electrical | Electrical | Design | Safety | Electrical: Raceways | Encase new underground conduit duct banks in concrete which has been colored red on the top surface. | Alan Speegle (Southern Co.)
232 | Raceways | Electrical | Electrical | Design | Safety | Electrical: Raceways | Require a red colored warning tape to be placed approximately 12 inches above direct buried power cables. | Alan Speegle (Southern Co.)
233 | Cables | Electrical | Electrical | Design | Safety | Electrical: Cables | Proper color coding sequencing per the National Electrical Code is used for individual conductors of a cable (e.g., green ground and white or gray neutral). | Alan Speegle (Southern Co.)
234 | Cables | Electrical | Electrical | Design | Safety | Electrical: Cables | Cables are tagged on each end with the proper identification. | Alan Speegle (Southern Co.)
235 | Cables | Electrical | Electrical | Design | Safety | Electrical: Cables | Cable tags specified are permanent and easily readable. | Alan Speegle (Southern Co.)
236 | Cables | Electrical | Electrical | Design | Safety | Electrical: Cables | Medium voltage armored cables are properly color coded. | Alan Speegle (Southern Co.)
237 | Lighting | Civil | Electrical | Design | Safety | The design and erection sequence of lighting systems can affect the safety of construction workers. | Provide adequate illumination on projects during work at night. | Alan Speegle (Southern Co.)
238 | Lighting | Electrical | Electrical | Design | Safety | The design and erection sequence of lighting systems can affect the safety of construction workers. | Lighting is adequate to insure safe task performance by personnel. This includes general area lighting, instrument racks, pumps, valves, etc. | Alan Speegle (Southern Co.)
239 | Lighting | Electrical | Electrical | Design | Safety | The design and erection sequence of lighting systems can affect the safety of construction workers. | Compliance with Illuminating Engineering Society of North America (IESNA) guidelines. | Alan Speegle (Southern Co.)
240 | Lighting | Electrical | Electrical | Design | Safety | The design and erection sequence of lighting systems can affect the safety of construction workers. | Provide permanent electrical outlets on roofs to allow for future roof maintenance. | Alan Speegle (Southern Co.)
241 | Lighting | Electrical | Electrical | Design | Safety | The design and erection sequence of lighting systems can affect the safety of construction workers. | Phasing for lighting is mixed to avoid “stroboscopic” effect. | Alan Speegle (Southern Co.)
242 | Lighting | Electrical | Electrical | Design | Safety | The design and erection sequence of lighting systems can affect the safety of construction workers. | Adequate emergency lighting has been provided. This includes both exit lighting and emergency general area lighting. | Alan Speegle (Southern Co.)
243 | Lighting | Electrical | Electrical | Design | Safety | The design and erection sequence of lighting systems can affect the safety of construction workers. | Quartz or incandescent emergency lighting has been specified for lamp restrike ride through. | Alan Speegle (Southern Co.)
244 | Lighting | Electrical | Electrical | Design | Safety | The design and erection sequence of lighting systems can affect the safety of construction workers. | Design and schedule lighting systems to be erected with the structural framing. | Alan Speegle (Southern Co.)
245 | Communication System | Electrical | Electrical | Design | Safety | Electrical: Communication System | Paging system will support emergency personnel notification requirements. | Alan Speegle (Southern Co.)
246 | Communication System | Electrical | Electrical | Design | Safety | Electrical: Communication System | Emergency sirens or horns required for evacuation notification. | Alan Speegle (Southern Co.)
247 | Tagging and Signage | Electrical | Electrical | Design | Safety | Electrical: Tagging and Signage | Warning placards, labels, and decals are properly positioned. | Alan Speegle (Southern Co.)
248 | Tagging and Signage | Electrical | Electrical | Design | Safety | Electrical: Tagging and Signage | Warning signs are standardized throughout the project. | Alan Speegle (Southern Co.)
249 | Tagging and Signage | Electrical | Electrical | Design | Safety | Electrical: Tagging and Signage | Equipment nameplates accurately represent electrical device identification and function. | Alan Speegle (Southern Co.)
250 | Tagging and Signage | Electrical | Electrical | Design | Safety | Electrical: Tagging and Signage | Equipment nameplates are easily readable and properly positioned. | Alan Speegle (Southern Co.)
251 | Tagging and Signage | Electrical | Electrical | Design | Safety | Electrical: Tagging and Signage | Electrical equipment is compliant with National Fire Protection Association (NFPA) Standard 70E requirements. | Alan Speegle (Southern Co.)
252 | Technical Services | Electrical | Electrical | Design | Safety | Electrical: Technical Services | Protective relaying requirements have been reviewed and required settings installed in the equipment. | Alan Speegle (Southern Co.)
253 | Technical Services | Electrical | Electrical | Design | Safety | Electrical: Technical Services | Grounding study and recommendation completed and used for completion of plant grounding drawings. | Alan Speegle (Southern Co.)
254 | Technical Services | Electrical | Electrical | Design | Safety | Electrical: Technical Services | Equipment withstand and interrupt ratings are adequate to protect both equipment and personnel. | Alan Speegle (Southern Co.)
255 | Technical Services | Electrical | Electrical | Design | Safety | Electrical: Technical Services | Minimum power cable sizes have been specified for both fault withstand and continuous power rating. | Alan Speegle (Southern Co.)
256 | Technical Services | Electrical | Electrical | Design | Safety | Electrical: Technical Services | Station service load study performed to ensure that switchgear and buswork is adequate for the service. | Alan Speegle (Southern Co.)
257 | Coatings | Civil | Corosion Protection And Insulation | Design | Safety | The selection of coating materials can affect the safety and health of construction workers. | Specify high solids, and no, or low, V.O.C. coating systems. | Alan Speegle (Southern Co.)
258 | Erection | Civil | Corosion Protection And Insulation | Design | Safety | The erection sequence or placement procedures for furnishings and finishes can affect the safety of construction workers. | Design and schedule materials and equipment to be painted and/or insulated prior to erection or placement. | Alan Speegle (Southern Co.)
259 | Design | Civil | Handrail, Guardrail | Design | Safety | Inadequately designed handrails, guardrails, and stairrails can lead to obstruction and fall hazards for construction & operations workers. | Mount the toprails on top of the posts, rather than on the side of the posts. | Alan Speegle (Southern Co.)
260 | Design | Civil | Handrail, Guardrail | Design | Safety | Inadequately designed handrails, guardrails, and stairrails can lead to obstruction and fall hazards for construction & operations workers. | Provide a minimum clearance of 1-1/2 inches along the top and sides of the toprail. | Alan Speegle (Southern Co.)
261 | Design | Civil | Handrail, Guardrail | Design | Safety | Inadequately designed handrails, guardrails, and stairrails can lead to obstruction and fall hazards for construction & operations workers. | Do not attach equipment or other objects to the toprails. | Alan Speegle (Southern Co.)
262 | Design | Civil | Handrail, Guardrail | Design | Safety | Inadequately designed handrails, guardrails, and stairrails can lead to obstruction and fall hazards for construction & operations workers. | Connect railing members by welding rather than bolts. | Alan Speegle (Southern Co.)
263 | Design | Civil | Handrail, Guardrail | Design | Safety | Inadequately designed handrails, guardrails, and stairrails can lead to obstruction and fall hazards for construction & operations workers. | Design joints and railing ends to be rounded and smooth. | Alan Speegle (Southern Co.)
264 | Design | Civil | Handrail, Guardrail | Design | Safety | Inadequately designed handrails, guardrails, and stairrails can lead to obstruction and fall hazards for construction & operations workers. | Design handrails and the top rails of a stairrail system to withstand at least 200 lbs. applied within 2 in. of the top edge in any downward or outward direction, at any point along the top edge. | Alan Speegle (Southern Co.)
265 | Design | Civil | Handrail, Guardrail | Design | Safety | Inadequately designed handrails, guardrails, and stairrails can lead to obstruction and fall hazards for construction & operations workers. | Provide continuous toeboards along the length of guardrails. | Alan Speegle (Southern Co.)
266 | Design | Civil | Handrail, Guardrail | Design | Safety | Inadequately designed handrails, guardrails, and stairrails can lead to obstruction and fall hazards for construction & operations workers. | Use a uniform railing height throughout the project. | Alan Speegle (Southern Co.)
267 | Railing Dimensions | Civil | Handrail, Guardrail | Design | Safety | Handrail and railing dimensions can affect the safety of construction workers. | When the top edge of a stairrail system also serves as a handrail, the height of the top edge should be between 36 and 37 in. from the upper surface of the stairrail to the surface of the stair. | Alan Speegle (Southern Co.)
268 | Railing Dimensions | Civil | Handrail, Guardrail | Design | Safety | Handrail and railing dimensions can affect the safety of construction workers. | Design the height of handrails to be between 30 and 37 inches from the upper surface of the handrail to the surface of the tread. | Alan Speegle (Southern Co.)
269 | Railing Dimensions | Civil | Handrail, Guardrail | Design | Safety | Handrail and railing dimensions can affect the safety of construction workers. | Design intermediate vertical members on stairrails and guardrails to be at most 19 inches apart. | Alan Speegle (Southern Co.)
270 | Openings | Civil | Handrail, Guardrail | Design | Safety | Roof openings can create fall hazards for construction workers if they are numerous or not adequately guarded. Stairs and elevated walkways and platforms can lead to falls during construction before handrails, guardrails, and stairrails are erected. | Provide permanent guardrails around floor openings. | Alan Speegle (Southern Co.)
271 | Openings | Civil | Handrail, Guardrail | Design | Safety | Roof openings can create fall hazards for construction workers if they are numerous or not adequately guarded. Stairs and elevated walkways and platforms can lead to falls during construction before handrails, guardrails, and stairrails are erected. | Provide permanent guardrails around roof openings. | Alan Speegle (Southern Co.)
272 | Openings | Civil | Handrail, Guardrail | Design | Safety | Roof openings can create fall hazards for construction workers if they are numerous or not adequately guarded. Stairs and elevated walkways and platforms can lead to falls during construction before handrails, guardrails, and stairrails are erected. | Design and schedule handrails, guardrails, and stairrails to be erected as part of the structural steel erection. | Alan Speegle (Southern Co.)
273 | Stairs | Civil | Handrail, Guardrail | Design | Safety |  | Provide a guardrail around roof accesses and roof work areas. | Alan Speegle (Southern Co.)
274 | Controls | Mechanical | Mechanical/Hvac | Design | Safety | Mechanical/HVAC controls can create safety hazards for construction workers if they protrude into passageways, or are hard to operate, hidden, or inaccessible. | Position equipment controls and control panels away from passageways and work areas. | Alan Speegle (Southern Co.)
275 | Controls | Mechanical | Mechanical/Hvac | Design | Safety | Mechanical/HVAC controls can create safety hazards for construction workers if they protrude into passageways, or are hard to operate, hidden, or inaccessible. | Indicate on the contract drawings the location of equipment shut-off valves and switches for existing utilities. Allow the constructor access to these locations for emergency situations. | Alan Speegle (Southern Co.)
276 | Controls | Mechanical | Mechanical/Hvac | Design | Safety | Mechanical/HVAC controls can create safety hazards for construction workers if they protrude into passageways, or are hard to operate, hidden, or inaccessible. | Place electrical circuit breaker boxes in sight of the equipment which they affect. | Alan Speegle (Southern Co.)
277 | Controls | Mechanical | Mechanical/Hvac | Design | Safety | Mechanical/HVAC controls can create safety hazards for construction workers if they protrude into passageways, or are hard to operate, hidden, or inaccessible. | Provide clearly marked and identified emergency controls and displays. | Alan Speegle (Southern Co.)
278 | Controls | Mechanical | Mechanical/Hvac | Design | Safety | Mechanical/HVAC controls can create safety hazards for construction workers if they protrude into passageways, or are hard to operate, hidden, or inaccessible. | Allow adequate access to equipment controls for ease of operation. | Alan Speegle (Southern Co.)
279 | Electrical/Grounding | Electrical | Mechanical/Hvac | Design | Safety | Adequate electrical protection and grounding of equipment is essential to prevent electrical shock hazards. | Ensure that all equipment is grounded and protected against lightning. | Alan Speegle (Southern Co.)
280 | Electrical/Grounding | Electrical | Mechanical/Hvac | Design | Safety | Adequate electrical protection and grounding of equipment is essential to prevent electrical shock hazards. | Isolate all live conductors and equipment from accidental contact. | Alan Speegle (Southern Co.)
281 | Electrical/Grounding | Electrical | Mechanical/Hvac | Design | Safety | Adequate electrical protection and grounding of equipment is essential to prevent electrical shock hazards. | Ensure an adequate interrupting rating to protect all equipment. | Alan Speegle (Southern Co.)
282 | Equipment Cooling | Electrical; Mechanical | Mechanical/Hvac | Design | Safety | Inadequate cooling and ventilation of electrical equipment can lead to fire hazards during the construction phase. | Ensure that all electrical equipment is adequately cooled and ventilated. | Alan Speegle (Southern Co.)
283 | Equipment Location | Mechanical | Mechanical/Hvac | Design | Safety | The location of mechanical and HVAC systems within a project can lead to fall, ergonomic, and other safety hazards for construction workers. | Minimize the amount of overhead work. | Alan Speegle (Southern Co.)
284 | Equipment Location | Mechanical | Mechanical/Hvac | Design | Safety | The location of mechanical and HVAC systems within a project can lead to fall, ergonomic, and other safety hazards for construction workers. | Locate underground equipment in an area easily accessible for excavation. Allow sufficient area around the excavation for stockpiling the soil. | Alan Speegle (Southern Co.)
285 | Equipment Location | Mechanical | Mechanical/Hvac | Design | Safety | The location of mechanical and HVAC systems within a project can lead to fall, ergonomic, and other safety hazards for construction workers. | Locate rooftop mechanical/HVAC equipment away from the structure's edge and skylights. | Alan Speegle (Southern Co.)
286 | Equipment Location | Mechanical | Mechanical/Hvac | Design | Safety | The location of mechanical and HVAC systems within a project can lead to fall, ergonomic, and other safety hazards for construction workers. | Ensure that equipment located in a hazardous area meets the requirements for the area's hazard classification. | Alan Speegle (Southern Co.)
287 | Equipment Materials | Mechanical | Mechanical/Hvac | Design | Safety | Mechanical and HVAC systems which are not constructed of materials adequate for the expected construction environment and loading create safety hazards for construction workers. | Design all mechanical equipment and HVAC components to meet the anticipated material, corrosion, and loading requirements of the construction site. | Alan Speegle (Southern Co.)
288 | Equipment Supports | Mechanical | Mechanical/Hvac | Design | Safety | Mechanical and HVAC systems and their supports which are not designed to withstand all anticipated construction loading present collapse and fall hazards to construction workers. | Design overhead equipment and their supports to hold up the weight of a construction worker. | Alan Speegle (Southern Co.)
289 | Equipment Supports | Mechanical | Mechanical/Hvac | Design | Safety | Mechanical and HVAC systems and their supports which are not designed to withstand all anticipated construction loading present collapse and fall hazards to construction workers. | Specify the material hoist or crane loading capacity to be clearly stenciled onto the hoist or crane beams or rails. | Alan Speegle (Southern Co.)
290 | Piping | Mechanical | Mechanical/Hvac | Design | Safety | Piping elements which are not designed with consideration of the connecting mechanical and HVAC units can lead to safety hazards during construction and initial startup phases. | Provide purging cycles and special interlocks for all gas- and oil-fired equipment. | Alan Speegle (Southern Co.)
291 | Piping | Mechanical | Mechanical/Hvac | Design | Safety | Piping elements which are not designed with consideration of the connecting mechanical and HVAC units can lead to safety hazards during construction and initial startup phases. | Ensure that the shut-off head on all pumps is compatible with the associated piping. | Alan Speegle (Southern Co.)
292 | Piping | Mechanical | Mechanical/Hvac | Design | Safety | Piping elements which are not designed with consideration of the connecting mechanical and HVAC units can lead to safety hazards during construction and initial startup phases. | Design piping systems which feed tanks, chests, and large walk-in type equipment to prevent inadvertent system activation. (LO/TO procedures) | Alan Speegle (Southern Co.)
293 | Piping | Mechanical | Mechanical/Hvac | Design | Safety | Piping elements which are not designed with consideration of the connecting mechanical and HVAC units can lead to safety hazards during construction and initial startup phases. | Ensure that safety relief valves exhaust and drain away from passageways and work areas. | Alan Speegle (Southern Co.)
294 | Valves | Mechanical | Mechanical/Hvac | Design | Safety | Valve location and operation can lead to safety hazards for construction workers during the construction and initial startup phases. | Locate valves such that they can be operated easily, or so that a standard type of operating device can be installed. Consider using remote valve operators. | Alan Speegle (Southern Co.)
295 | Valves | Mechanical | Mechanical/Hvac | Design | Safety | Valve location and operation can lead to safety hazards for construction workers during the construction and initial startup phases. | Provide remotely operated valves or valves with extension handles when valves are located near hazardous materials or in confined spaces. | Alan Speegle (Southern Co.)
296 | Valves | Mechanical | Mechanical/Hvac | Design | Safety | Valve location and operation can lead to safety hazards for construction workers during the construction and initial startup phases. | Provide a safety valve on the discharge of positive displacement type air compressors and multi-stage centrifugal compressors to avoid over-pressurization in case the discharge valve is closed. | Alan Speegle (Southern Co.)
297 | Valves | Mechanical | Mechanical/Hvac | Design | Safety | Valve location and operation can lead to safety hazards for construction workers during the construction and initial startup phases. | Provide relief valves for heat exchangers and chiller refrigerant. | Alan Speegle (Southern Co.)
298 | Ventilating Equipment | Mechanical | Mechanical/Hvac | Design | Safety | Adequate ventilation for construction workers during the construction phase is essential for a safe work environment. | Design ventilating and lighting fixtures in a mechanical room and confined space to be operated by the same switch. | Alan Speegle (Southern Co.)
299 | Ventilating Equipment | Mechanical | Mechanical/Hvac | Design | Safety | Adequate ventilation for construction workers during the construction phase is essential for a safe work environment. | Provide ventilation systems in mechanical rooms and confined spaces which are temperature, oxygen depletion, or refrigerant controlled. | Alan Speegle (Southern Co.)
300 | Ventilating Equipment | Mechanical | Mechanical/Hvac | Design | Safety | Adequate ventilation for construction workers during the construction phase is essential for a safe work environment. | Design and schedule ventilation and illumination in stair shafts to be operable during construction. | Alan Speegle (Southern Co.)
301 | Ventilating Equipment | Mechanical | Mechanical/Hvac | Design | Safety | Adequate ventilation for construction workers during the construction phase is essential for a safe work environment. | Provide ventilation systems around fueled equipment operating indoors. | Alan Speegle (Southern Co.)
302 | Work Area A | Mechanical | Mechanical/Hvac | Design | Safety | An enclosed or congested work area surrounding mechanical and HVAC equipment can affect the safety of workers during installation and maintenance of the equipment. | Do not locate mechanical equipment in or directly adjacent to passageways. | Alan Speegle (Southern Co.)
303 | Work Area A | Mechanical | Mechanical/Hvac | Design | Safety | An enclosed or congested work area surrounding mechanical and HVAC equipment can affect the safety of workers during installation and maintenance of the equipment. | Provide a clear, unobstructed, spacious area around all permanent equipment. See Section 1926.403 of the Code of Federal Regulations for working clearances. | Alan Speegle (Southern Co.)
304 | Work Area A | Mechanical | Mechanical/Hvac | Design | Safety | An enclosed or congested work area surrounding mechanical and HVAC equipment can affect the safety of workers during installation and maintenance of the equipment. | Ensure that all equipment enclosures meet hazardous location classification requirements. | Alan Speegle (Southern Co.)
305 | Work Area A | Mechanical | Mechanical/Hvac | Design | Safety | An enclosed or congested work area surrounding mechanical and HVAC equipment can affect the safety of workers during installation and maintenance of the equipment. | Do not place machinery breathing equipment, oxygen sensor, refrigerant sensor, or refrigerant/fuel burning equipment in the same space unless a clean air source is provided. | Alan Speegle (Southern Co.)
306 | Work Area B | Mechanical | Mechanical/Hvac | Design | Safety | The floor area and support structure surrounding mechanical and HVAC systems can create safety hazards during placement of the equipment and work around the equipment. | Keep the finished floor around mechanical and HVAC equipment free of steps, blockouts, etc. | Alan Speegle (Southern Co.)
307 | Work Area B | Mechanical | Mechanical/Hvac | Design | Safety | The floor area and support structure surrounding mechanical and HVAC systems can create safety hazards during placement of the equipment and work around the equipment. | Place all equipment and related hardware on an elevated housekeeping pad above the finished floor level. | Alan Speegle (Southern Co.)
308 | Work Area B | Mechanical | Mechanical/Hvac | Design | Safety | The floor area and support structure surrounding mechanical and HVAC systems can create safety hazards during placement of the equipment and work around the equipment. | Locate lifting eyes, hoist, or crane above equipment to aid in the installation and maintenance of the equipment. | Alan Speegle (Southern Co.)
309 | Work Area B | Mechanical | Mechanical/Hvac | Design | Safety | The floor area and support structure surrounding mechanical and HVAC systems can create safety hazards during placement of the equipment and work around the equipment. | Minimize the number of wires, cables, and hoses laid on walking surfaces. Use elevated cable trays or hose supports. | Alan Speegle (Southern Co.)
310 | Work Area C | Mechanical | Mechanical/Hvac | Design | Safety | Work areas without adequate protection from equipment noise, electrical shock, or moving parts are hazardous for construction workers. | Specify mechanical and HVAC equipment which does not produce high noise levels while operating. See Section 1926.52 of the Code of Federal Regulations for acceptable noise levels. | Alan Speegle (Southern Co.)
311 | Work Area C | Mechanical | Mechanical/Hvac | Design | Safety | Work areas without adequate protection from equipment noise, electrical shock, or moving parts are hazardous for construction workers. | Provide guards around equipment to protect workers from moving parts. | Alan Speegle (Southern Co.)
312 | Work Area C | Mechanical | Mechanical/Hvac | Design | Safety | Work areas without adequate protection from equipment noise, electrical shock, or moving parts are hazardous for construction workers. | Provide guards around fan inlets/outlets and exhaust ports. | Alan Speegle (Southern Co.)
313 | Work Area C | Mechanical | Mechanical/Hvac | Design | Safety | Work areas without adequate protection from equipment noise, electrical shock, or moving parts are hazardous for construction workers. | Provide signs, lights, alarms, etc. as necessary to ensure safety near exposed equipment. | Alan Speegle (Southern Co.)
314 | Work Area C | Mechanical | Mechanical/Hvac | Design | Safety | Work areas without adequate protection from equipment noise, electrical shock, or moving parts are hazardous for construction workers. | Provide smoke detectors or insulation around equipment susceptible to fire. | Alan Speegle (Southern Co.)
315 | Erection | Mechanical | Mechanical/Hvac | Design | Safety | The erection or placement operations required for mechanical and HVAC systems can create safety hazards for construction workers. | Design and schedule new air conditioning and ventilating systems to be in use as early as possible in the construction phase. | Alan Speegle (Southern Co.)
316 | Erection | Mechanical | Mechanical/Hvac | Design | Safety | The erection or placement operations required for mechanical and HVAC systems can create safety hazards for construction workers. | Minimize the need for special or complicated equipment installation operations. | Alan Speegle (Southern Co.)
317 | Erection | Mechanical | Mechanical/Hvac | Design | Safety | The erection or placement operations required for mechanical and HVAC systems can create safety hazards for construction workers. | Design and schedule equipment to be painted and/or insulated prior to erection or installation. | Alan Speegle (Southern Co.)
318 | Erection | Mechanical | Mechanical/Hvac | Design | Safety | The erection or placement operations required for mechanical and HVAC systems can create safety hazards for construction workers. | Schedule new ventilating systems to be in use in areas in which painting or other coatings will be applied, prior to their application. | Alan Speegle (Southern Co.)
319 | Existing Structure | Mechanical | Mechanical/Hvac | Design | Safety | Working with and connecting to existing mechanical and HVAC systems presents safety hazards for construction workers. | Design and schedule safe tie-ins to existing utilities. | Alan Speegle (Southern Co.)
320 | Testing | Mechanical | Mechanical/Hvac | Design | Safety | Sufficient testing of mechanical and HVAC systems is essential to eliminate safety hazards due to failure of the systems. | Require systems, components, and welds to be tested to ensure they meet minimum requirements. Types of testing to consider: hydrostatic, radiographic, ultrasonic, magnaflux, weld sectioning, dye penetrant, halogen mass spectrometer, etc. | Alan Speegle (Southern Co.)
321 | Testing | Mechanical | Mechanical/Hvac | Design | Safety | Sufficient testing of mechanical and HVAC systems is essential to eliminate safety hazards due to failure of the systems. | Design for safety against possible equipment failures, such as desuperheated, control valve, or component failure. | Alan Speegle (Southern Co.)
322 | Controls/Valves A | Mechanical; I&C | Piping | Design | Safety | The design of piping controls and valves can lead to safety hazards for construction workers. | A bypass around a reducing valve should not have greater capacity than the reducing valve unless the piping is adequately protected by relief valves or meets the requirements of the higher pressure system. | Alan Speegle (Southern Co.)
323 | Controls/Valves A | Mechanical; I&C | Piping | Design | Safety | The design of piping controls and valves can lead to safety hazards for construction workers. | Provide proper protection to prevent injury or damage caused by escaping fluid from relief or safety valves if vented to the atmosphere. | Alan Speegle (Southern Co.)
324 | Controls/Valves A | Mechanical; I&C | Piping | Design | Safety | The design of piping controls and valves can lead to safety hazards for construction workers. | Prevent "water hammer" by providing air vents, surge valves, surge chambers, or delayed or timed valve operation. | Alan Speegle (Southern Co.)
325 | Controls/Valves A | Mechanical; I&C | Piping | Design | Safety | The design of piping controls and valves can lead to safety hazards for construction workers. | Position controls away from passageways and work areas. | Alan Speegle (Southern Co.)
326 | Controls/Valves B | Mechanical; I&C | Piping | Design | Safety | The design of piping controls and valves can lead to safety hazards for construction workers. | Locate valve controls so that handles can be reached easily, or so that a standard type operating device can be installed. | Alan Speegle (Southern Co.)
327 | Controls/Valves B | Mechanical; I&C | Piping | Design | Safety | The design of piping controls and valves can lead to safety hazards for construction workers. | Indicate on the contract drawings the location of shut-off valves and switches for existing systems. Allow and provide access by the constructor to the locations. | Alan Speegle (Southern Co.)
328 | Controls/Valves B | Mechanical; I&C | Piping | Design | Safety | The design of piping controls and valves can lead to safety hazards for construction workers. | Ensure that control valve specifications meet the piping specifications for body rating, body material (corrosion and hazardous services), and flange type. | Alan Speegle (Southern Co.)
329 | Controls/Valves B | Mechanical; I&C | Piping | Design | Safety | The design of piping controls and valves can lead to safety hazards for construction workers. | Size control valves with consideration of noise level. | Alan Speegle (Southern Co.)
330 | Controls/Valves B | Mechanical; I&C | Piping | Design | Safety | The design of piping controls and valves can lead to safety hazards for construction workers. | Provide a tag or other positive i.d. of the appropriate pressure, temperature, etc. on all valves. | Alan Speegle (Southern Co.)
331 | Controls/Valves C | Mechanical | Piping | Design | Safety | The design of piping controls and valves can lead to safety hazards for construction workers. | Direct safety relief valve exhausts away from passageways and work areas. | Alan Speegle (Southern Co.)
332 | Controls/Valves C | Mechanical | Piping | Design | Safety | The design of piping controls and valves can lead to safety hazards for construction workers. | Consider rupture disks as a safety device either in conjunction with or as a substitute for safety valves, or to act as an explosion door on vessels and piping subject to explosions. | Alan Speegle (Southern Co.)
333 | Controls/Valves C | Mechanical | Piping | Design | Safety | The design of piping controls and valves can lead to safety hazards for construction workers. | Check safety relief valves against the piping process to determine if the valves are required to be A.S.M.E. code stamped. | Alan Speegle (Southern Co.)
334 | Controls/Valves C | Mechanical | Piping | Design | Safety | The design of piping controls and valves can lead to safety hazards for construction workers. | Provide relief valves between each pair of sectionalizing valves on lines containing liquids and subject to being both isolated and heated, such as heat exchangers, liquefied gas piping, etc. | Alan Speegle (Southern Co.)
335 | Controls/Valves C | Mechanical | Piping | Design | Safety | The design of piping controls and valves can lead to safety hazards for construction workers. | Use a globe or throttle valve on a bypass. | Alan Speegle (Southern Co.)
336 | Drains | Mechanical | Piping | Design | Safety | Drains can create tripping and slipping hazards for construction workers. | Design covers over sumps and drains to be flush with the floor level. | Alan Speegle (Southern Co.)
337 | Drains | Mechanical | Piping | Design | Safety | Drains can create tripping and slipping hazards for construction workers. | Design area drains to be trapped or valved shut to avoid the spread of fire in case of a ruptured pipe. | Alan Speegle (Southern Co.)
338 | Drains | Mechanical | Piping | Design | Safety | Drains can create tripping and slipping hazards for construction workers. | Route piping drains and overflows to trench drains so that floors remain dry. | Alan Speegle (Southern Co.)
339 | Drains | Mechanical | Piping | Design | Safety | Drains can create tripping and slipping hazards for construction workers. | Pipe pump seal water in a manner to avoid slipping, e.g. case drains/base plates to hubs. | Alan Speegle (Southern Co.)
340 | Hazardous Fluids | Mechanical | Piping | Design | Safety | Piping systems which contain hazardous fluids can present safety hazards for construction workers. | Design piping which carries hazardous fluids to have a double lock-nut capability. Allow for a pressure bleed on trapped hazardous fluids, especially steam and condensate bypasses. | Alan Speegle (Southern Co.)
341 | Hazardous Fluids | Mechanical | Piping | Design | Safety | Piping systems which contain hazardous fluids can present safety hazards for construction workers. | Eliminate drainage of slippery and dangerous chemicals into passageways and work areas. | Alan Speegle (Southern Co.)
342 | Hazardous Fluids | Mechanical | Piping | Design | Safety | Piping systems which contain hazardous fluids can present safety hazards for construction workers. | Avoid routing dangerous fluids over equipment, control boards, aisles, and operator areas to avoid injury in case of a pipe leak. | Alan Speegle (Southern Co.)
343 | Pipes A | Mechanical | Piping | Design | Safety | The design of piping materials and welds, and the identification of piping contents, can affect the safety of construction workers. | Check that foreign piping components are compatible with other piping system components. | Alan Speegle (Southern Co.)
344 | Pipes A | Mechanical | Piping | Design | Safety | The design of piping materials and welds, and the identification of piping contents, can affect the safety of construction workers. | Color code the pipes to easily identify their contents. | Alan Speegle (Southern Co.)
345 | Pipes A | Mechanical | Piping | Design | Safety | The design of piping materials and welds, and the identification of piping contents, can affect the safety of construction workers. | Show the pipe content flow direction on the contract drawings so that the first valve upstream of an emergency can be easily located. | Alan Speegle (Southern Co.)
346 | Pipes A | Mechanical | Piping | Design | Safety | The design of piping materials and welds, and the identification of piping contents, can affect the safety of construction workers. | Avoid interior welds in large pipes and tanks, and ensure that welding conditions are appropriate for the type of pipe material, e.g. alloy piping systems requiring PWHT/preheat. | Alan Speegle (Southern Co.)
347 | Pipes A | Mechanical | Piping | Design | Safety | The design of piping materials and welds, and the identification of piping contents, can affect the safety of construction workers. | Specify the use of hose racks for all areas requiring hoses. | Alan Speegle (Southern Co.)
348 | Pipes B | Mechanical | Piping | Design | Safety | Piping systems which do not meet design code regulations and which are not designed for the appropriate construction conditions create safety hazards for construction workers. | Design piping system components to meet all national, state, and local building code requirements. | Alan Speegle (Southern Co.)
349 | Pipes B | Mechanical | Piping | Design | Safety | Piping systems which do not meet design code regulations and which are not designed for the appropriate construction conditions create safety hazards for construction workers. | Do not make direct cross connections between drinking water or utility systems and plant or process streams. | Alan Speegle (Southern Co.)
350 | Pipes B | Mechanical | Piping | Design | Safety | Piping systems which do not meet design code regulations and which are not designed for the appropriate construction conditions create safety hazards for construction workers. | Design trap discharge piping for the pressure of the piping system being trapped unless protected by vents or relief valves. | Alan Speegle (Southern Co.)
351 | Pipes B | Mechanical | Piping | Design | Safety | Piping systems which do not meet design code regulations and which are not designed for the appropriate construction conditions create safety hazards for construction workers. | Minimize pockets in piping systems. Trap all pockets. | Alan Speegle (Southern Co.)
352 | Pipes B | Mechanical | Piping | Design | Safety | Piping systems which do not meet design code regulations and which are not designed for the appropriate construction conditions create safety hazards for construction workers. | Minimize flanges in piping under high pressure, or which contains explosive or lethal gases. | Alan Speegle (Southern Co.)
353 | Pipes C | Mechanical | Piping | Design | Safety | Inadequate consideration of the entire piping system design can lead to safety hazards for construction workers. | Provide adequate safety measures in the event of possible equipment failure. | Alan Speegle (Southern Co.)
354 | Pipes C | Mechanical | Piping | Design | Safety | Inadequate consideration of the entire piping system design can lead to safety hazards for construction workers. | Design adequate protection against over-pressure for all piping components. | Alan Speegle (Southern Co.)
355 | Pipes C | Mechanical | Piping | Design | Safety | Inadequate consideration of the entire piping system design can lead to safety hazards for construction workers. | Locate explosive or lethal gas lines outside of buildings, or in areas properly ventilated. Use all-welded construction to reduce chances of a leak. | Alan Speegle (Southern Co.)
356 | Pipes C | Mechanical | Piping | Design | Safety | Inadequate consideration of the entire piping system design can lead to safety hazards for construction workers. | Design all impoundments for liquids to provide a means or facility to accommodate emergency bypass conditions. | Alan Speegle (Southern Co.)
357 | Pipes C | Mechanical | Piping | Design | Safety | Inadequate consideration of the entire piping system design can lead to safety hazards for construction workers. | Design pipe materials to be chemically resistant to the fluids the system is designed to carry. | Alan Speegle (Southern Co.)
358 | Piping Location | Mechanical | Piping | Design | Safety | The location of piping components throughout a project can affect the safety of construction workers. | Route piping lines below electrical/instrumentation cable trays to prevent the chance of electrical shock due to leaking pipes. | Alan Speegle (Southern Co.)
359 | Piping Location | Mechanical | Piping | Design | Safety | The location of piping components throughout a project can affect the safety of construction workers. | Minimize the amount of overhead work. | Alan Speegle (Southern Co.)
360 | Piping Location | Mechanical | Piping | Design | Safety | The location of piping components throughout a project can affect the safety of construction workers. | Locate piping lines which are under very high pressure or contain explosive or lethal gases on the outside of buildings or in areas properly ventilated and guarded. | Alan Speegle (Southern Co.)
361 | Piping Location | Mechanical | Piping | Design | Safety | The location of piping components throughout a project can affect the safety of construction workers. | Do not locate piping in rooms containing high voltage equipment, bare wires, or bus bars. | Alan Speegle (Southern Co.)
362 | Piping Supports | Mechanical | Piping | Design | Safety | A lack of sufficient support for piping systems can create collapse and fall hazards for construction workers. | Route piping to avoid "head knockers" (6'-6" min. above grade) and tripping hazards. | Alan Speegle (Southern Co.)
363 | Piping Supports | Mechanical | Piping | Design | Safety | A lack of sufficient support for piping systems can create collapse and fall hazards for construction workers. | Provide fall restraint cables along the length of overhead piping runs. | Alan Speegle (Southern Co.)
364 | Piping Supports | Mechanical | Piping | Design | Safety | A lack of sufficient support for piping systems can create collapse and fall hazards for construction workers. | Design overhead piping and supports to hold up a worker. | Alan Speegle (Southern Co.)
365 | Piping Supports | Mechanical | Piping | Design | Safety | A lack of sufficient support for piping systems can create collapse and fall hazards for construction workers. | Provide for thermal expansion of the piping by adding pipe bends, offsets, etc. | Alan Speegle (Southern Co.)
366 | Piping Supports | Mechanical | Piping | Design | Safety | A lack of sufficient support for piping systems can create collapse and fall hazards for construction workers. | Design steam lines with drips or freeblows to prevent "steam hammer" or "slugging". | Alan Speegle (Southern Co.)
367 | Piping Supports | Mechanical | Piping | Design | Safety | A lack of sufficient support for piping systems can create collapse and fall hazards for construction workers. | Design cross connections between low and high pressure systems with one or more of the following valves: double valves (both to have high pressure rating), high pressure check valve, normally open vent valve between double valves, or a relief valve on lo | Alan Speegle (Southern Co.)
368 | Erection | Mechanical | Piping | Design | Safety | Applying paint or insulation to elevated piping systems can lead to fall hazards for construction workers. Large pipe sections which lack adequate connection points for lifting, and lack restraint from rolling, can create safety hazards for workers durin | Design and schedule piping materials to be painted and/or insulated prior to erection or installation. | Alan Speegle (Southern Co.)
369 | Erection | Mechanical | Piping | Design | Safety | Applying paint or insulation to elevated piping systems can lead to fall hazards for construction workers. Large pipe sections which lack adequate connection points for lifting, and lack restraint from rolling, can create safety hazards for workers durin | Design large pipe sections to be oval or have one flatten portion to prevent rolling. | Alan Speegle (Southern Co.)
370 | Erection | Mechanical | Piping | Design | Safety | Applying paint or insulation to elevated piping systems can lead to fall hazards for construction workers. Large pipe sections which lack adequate connection points for lifting, and lack restraint from rolling, can create safety hazards for workers durin | Design in connection points on piping sections for lifting operations. Consider designing the connection points such that after pipe installation they can be used to connect the pipe sections. | Alan Speegle (Southern Co.)
371 | Existing Structure | Mechanical | Piping | Design | Safety | Working with and connecting to existing piping systems presents safety hazards for construction workers. | Design and schedule safe tie-ins to existing utilities. Ensure that the tie-in is appropriate for the piping contents and system. (stopple/hot top/cold cut, rubber plug and weld flange/unbolt) | Alan Speegle (Southern Co.)
372 | Existing Structure | Mechanical | Piping | Design | Safety | Working with and connecting to existing piping systems presents safety hazards for construction workers. | Use bolted rather than welded connections when working around existing flammable structures. | Alan Speegle (Southern Co.)
373 | Existing Structure | Mechanical | Piping | Design | Safety | Working with and connecting to existing piping systems presents safety hazards for construction workers. | Minimize the need for "hot work" permits by providing adequate buffer from existing piping systems. | Alan Speegle (Southern Co.)
374 | Fire Hazards | Mechanical | Piping | Design | Safety | The scheduled construction of new fire water systems, or demolition of existing systems, can lead to fire hazards on the construction project. | For taller buildings, design and schedule the fire water system to be installed early in the construction phase. | Alan Speegle (Southern Co.)
375 | Fire Hazards | Mechanical | Piping | Design | Safety | The scheduled construction of new fire water systems, or demolition of existing systems, can lead to fire hazards on the construction project. | Design and schedule an underground fire water system to be constructed throughout the project site before construction begins. | Alan Speegle (Southern Co.)
376 | Fire Hazards | Mechanical | Piping | Design | Safety | The scheduled construction of new fire water systems, or demolition of existing systems, can lead to fire hazards on the construction project. | Minimize downtime periods of existing automatic sprinkler systems. | Alan Speegle (Southern Co.)
377 | Testing | Mechanical | Piping | Design | Safety | Piping material and system performance testing is essential to eliminate construction site safety hazards. | Require performance testing of the piping system, components, and welds using such tests as hydrostatic, radiographic, ultrasonic, magnaflux, weld sectioning, dye penetrant, etc. | Alan Speegle (Southern Co.)
378 | Testing | Mechanical | Piping | Design | Safety | Piping material and system performance testing is essential to eliminate construction site safety hazards. | Require a stress analysis to be performed on applicable systems. | Alan Speegle (Southern Co.)
379 | Testing | Mechanical | Piping | Design | Safety | Piping material and system performance testing is essential to eliminate construction site safety hazards. | Ensure that the shut-off head on all pumps is consistent with the associated piping. | Alan Speegle (Southern Co.)
380 | Testing | Mechanical | Piping | Design | Safety | Piping material and system performance testing is essential to eliminate construction site safety hazards. | Design piping systems which feed tanks, chests, and large walk-in type equipment to prevent inadvertent system activation. | Alan Speegle (Southern Co.)
381 | Underground Lines A | Mechanical | Piping | Design | Safety | New and existing below-grade piping lines present hazards during excavation, pile driving, and drilling operations. | Locate underground lines in areas easily accessible for excavation. Allow sufficient area around the excavations for stockpiling and transporting the soil. | Alan Speegle (Southern Co.)
382 | Underground Lines A | Mechanical | Piping | Design | Safety | New and existing below-grade piping lines present hazards during excavation, pile driving, and drilling operations. | When new piping lines are to be placed below existing concrete surfaces, roads, or other traffic areas, design the lines so that they may be placed using trenchless technologies. | Alan Speegle (Southern Co.)
383 | Underground Lines A | Mechanical | Piping | Design | Safety | New and existing below-grade piping lines present hazards during excavation, pile driving, and drilling operations. | Note on the contract drawings the level of certainty and source of information on the location and size of existing underground lines. | Alan Speegle (Southern Co.)
384 | Underground Lines A | Mechanical | Piping | Design | Safety | New and existing below-grade piping lines present hazards during excavation, pile driving, and drilling operations. | On the contract drawings, mark a clear zone around existing underground lines. | Alan Speegle (Southern Co.)
385 | Underground Lines A | Mechanical | Piping | Design | Safety | New and existing below-grade piping lines present hazards during excavation, pile driving, and drilling operations. | Require hand excavation when near existing underground utilities. | Alan Speegle (Southern Co.)
386 | Underground Lines B | Mechanical | Piping | Design | Safety | Existing underground lines which are in service during construction present safety hazards for construction workers. | Protect underground lines from crushing by use of sleeves or slabs, or by providing guard posts to prevent travel over them. | Alan Speegle (Southern Co.)
387 | Underground Lines B | Mechanical | Piping | Design | Safety | Existing underground lines which are in service during construction present safety hazards for construction workers. | Provide over-sized pipe sleeves around lines under railroad tracks and highways to avoid damage to the tracks or roadbed in case of a leak. | Alan Speegle (Southern Co.)
388 | Underground Lines B | Mechanical | Piping | Design | Safety | Existing underground lines which are in service during construction present safety hazards for construction workers. | Encase new underground lines in red concrete. | Alan Speegle (Southern Co.)
389 | Underground Lines B | Mechanical | Piping | Design | Safety | Existing underground lines which are in service during construction present safety hazards for construction workers. | Require a brightly colored warning tape to be placed along underground lines approximately 12 inches above the lines. | Alan Speegle (Southern Co.)
390 | Underground Lines B | Mechanical | Piping | Design | Safety | Existing underground lines which are in service during construction present safety hazards for construction workers. | Provide anchors or tie-downs for piping with push-type joints or other mechanical joints. | Alan Speegle (Southern Co.)
391 | Access | Civil | General Arrangement/Project Layout | Design | Safety | Limited access to elevated walkways and platforms can prohibit timely response and efficient maneuverability into and out of the areas in emergency situations. | Provide the constructor with floor and roof design loads for use in determining material stockpile locations and heavy equipment maneuverability. | Alan Speegle (Southern Co.)
392 | Electrical | Electrical; Civil | General Arrangement/Project Layout | Design | Safety | The location and layout of electrical rooms, and the positioning of electrical controls, can create electrical shock and other safety hazards for construction & operations workers. | Provide adequate passageways and access areas around all equipment in control, electrical, and electronic rooms. | Alan Speegle (Southern Co.)
393 | Electrical | Electrical | General Arrangement/Project Layout | Design | Safety | The location and layout of electrical rooms, and the positioning of electrical controls, can create electrical shock and other safety hazards for construction & operations workers. | Locate electrical circuit breaker boxes in sight of the equipment it affects. | Alan Speegle (Southern Co.)
394 | Electrical | Electrical; Civil | General Arrangement/Project Layout | Design | Safety | The location and layout of electrical rooms, and the positioning of electrical controls, can create electrical shock and other safety hazards for construction & operations workers. | Do not locate electrical rooms under pipes carrying liquids. | Alan Speegle (Southern Co.)
395 | Emergency Access | Civil | General Arrangement/Project Layout | Design | Safety | Emergency access to all parts of the project site is essential to provide prompt and adequate response to accidents and injuries. | Allow for at least two formal, controlled intersections at access points to the site. | Alan Speegle (Southern Co.)
396 | Emergency Access | Civil | General Arrangement/Project Layout | Design | Safety | Emergency access to all parts of the project site is essential to provide prompt and adequate response to accidents and injuries. | Orient the project to allow for the construction of temporary roads, fire lanes, and approach roads during construction. | Alan Speegle (Southern Co.)
397 | Floor Plan | Civil | General Arrangement/Project Layout | Design | Safety | A building's floor plan can lead to fall hazards if there are numerous offsets of varying size, floor levels varying in size or shape, or if the size and layout does not meet local building codes. | To minimize the risk of falling, minimize the number of offsets, and make the offsets a consistent size and as large as possible. | Alan Speegle (Southern Co.)
398 | Floor Plan | Civil | General Arrangement/Project Layout | Design | Safety | A building's floor plan can lead to fall hazards if there are numerous offsets of varying size, floor levels varying in size or shape, or if the size and layout does not meet local building codes. | Ensure that the building height and area per floor meet all local building code requirements for the type of construction used. | Alan Speegle (Southern Co.)
399 | Floor Plan | Civil | General Arrangement/Project Layout | Design | Safety | A building's floor plan can lead to fall hazards if there are numerous offsets of varying size, floor levels varying in size or shape, or if the size and layout does not meet local building codes. | Group floor openings together to create one larger opening rather than many smaller openings. | Alan Speegle (Southern Co.)
400 | Floor Plan | Civil | General Arrangement/Project Layout | Design | Safety | A building's floor plan can lead to fall hazards if there are numerous offsets of varying size, floor levels varying in size or shape, or if the size and layout does not meet local building codes. | Locate floor openings away from passageways, work areas, and the structure perimeter. | Alan Speegle (Southern Co.)
401 | Materials | Civil; Mechanical; Electrical; I&C | General Arrangement/Project Layout | Design | Safety | Construction materials can be hazardous to construction workers if the materials are flammable, contain toxic substances, or do not meet their specified use requirements. | Ensure that specified materials of construction are appropriate for the flammability hazards which may be encountered on the work site. | Alan Speegle (Southern Co.)
402 | Materials | Civil; Mechanical; Electrical; I&C | General Arrangement/Project Layout | Design | Safety | Construction materials can be hazardous to construction workers if the materials are flammable, contain toxic substances, or do not meet their specified use requirements. | Do not specify materials which contain asbestos or other known hazardous substances. | Alan Speegle (Southern Co.)
403 | Materials | Civil; Mechanical; Electrical; I&C | General Arrangement/Project Layout | Design | Safety | Construction materials can be hazardous to construction workers if the materials are flammable, contain toxic substances, or do not meet their specified use requirements. | Ensure that all materials meet the expected environmental and work site conditions. | Alan Speegle (Southern Co.)
404 | Mechanical | Mechanical | General Arrangement/Project Layout | Design | Safety | The location and layout of mechanical rooms, and the positioning of control valves and panels, can create obstruction and other safety hazards for construction workers. | Provide a clear, unobstructed, spacious work area around all permanent mechanical equipment. See Section 1926.403 of the Code of Federal Regulations. | Alan Speegle (Southern Co.)
405 | Mechanical | Mechanical | General Arrangement/Project Layout | Design | Safety | The location and layout of mechanical rooms, and the positioning of control valves and panels, can create obstruction and other safety hazards for construction workers. | Do not locate permanent mechanical equipment in or directly adjacent to passageways. | Alan Speegle (Southern Co.)
406 | Mechanical | Mechanical | General Arrangement/Project Layout | Design | Safety | The location and layout of mechanical rooms, and the positioning of control valves and panels, can create obstruction and other safety hazards for construction workers. | Position control valves and panels away from passageways and work areas. | Alan Speegle (Southern Co.)
407 | Mechanical | Mechanical | General Arrangement/Project Layout | Design | Safety | The location and layout of mechanical rooms, and the positioning of control valves and panels, can create obstruction and other safety hazards for construction workers. | Prevent access near hoist or crane electrification points and travel clearances. | Alan Speegle (Southern Co.)
408 | Mechanical | Civil | General Arrangement/Project Layout | Design | Safety | The location and layout of mechanical rooms, and the positioning of control valves and panels, can create obstruction and other safety hazards for construction workers. | Ball Mill structure has an overhead crane. This type area is new to plant employees. Consider all hazards associated with this new bridge crane. | Alan Speegle (Southern Co.)
409 | Power Lines | Electrical; Civil | General Arrangement/Project Layout | Design | Safety | Power lines which are in service during construction present an electrical shock hazard. Below-grade lines present a hazard when operating excavation, pile driving, and drilling equipment. Overhead lines are hazardous when operating cranes and other tal | Maintain a minimum clearance between the project and overhead power lines as outlined in Section 1926.950 of the Code of Federal Regulations. | Alan Speegle (Southern Co.)
410 | Power Lines | Electrical; Civil | General Arrangement/Project Layout | Design | Safety | Power lines which are in service during construction present an electrical shock hazard. Below-grade lines present a hazard when operating excavation, pile driving, and drilling equipment. Overhead lines are hazardous when operating cranes and other tal | Disconnect the power lines before construction begins. | Alan Speegle (Southern Co.)
411 | Power Lines | Electrical; Civil | General Arrangement/Project Layout | Design | Safety | Power lines which are in service during construction present an electrical shock hazard. Below-grade lines present a hazard when operating excavation, pile driving, and drilling equipment. Overhead lines are hazardous when operating cranes and other tal | Bury overhead power lines below grade before construction begins. | Alan Speegle (Southern Co.)
412 | Power Lines | Electrical; Civil | General Arrangement/Project Layout | Design | Safety | Power lines which are in service during construction present an electrical shock hazard. Below-grade lines present a hazard when operating excavation, pile driving, and drilling equipment. Overhead lines are hazardous when operating cranes and other tal | Re-route the power lines around the project site before construction begins. | Alan Speegle (Southern Co.)
413 | Power Lines | Electrical; Civil | General Arrangement/Project Layout | Design | Safety | Power lines which are in service during construction present an electrical shock hazard. Below-grade lines present a hazard when operating excavation, pile driving, and drilling equipment. Overhead lines are hazardous when operating cranes and other tal | Clearly mark the power lines with warning flags, tape, paint, chalk, etc., and note their location on the contract drawings. | Alan Speegle (Southern Co.)
414 | Space Layout | Civil | General Arrangement/Project Layout | Design | Safety | Rooms, walkways, platforms, etc. within a building which do not allow adequate egress or provide protection against hazardous materials can create safety hazards for construction workers. | Isolate from adjoining areas the storage areas for combustible and toxic materials, such as resins, paper, explosives, petroleum, plastics, etc. | Alan Speegle (Southern Co.)
415 | Space Layout | Civil | General Arrangement/Project Layout | Design | Safety | Rooms, walkways, platforms, etc. within a building which do not allow adequate egress or provide protection against hazardous materials can create safety hazards for construction workers. | Provide at least two means of egress on large maintenance platforms or walkways. | Alan Speegle (Southern Co.)
416 | Space Layout | Civil | General Arrangement/Project Layout | Design | Safety | Rooms, walkways, platforms, etc. within a building which do not allow adequate egress or provide protection against hazardous materials can create safety hazards for construction workers. | Minimize the number of confined spaces. Design access points to confined spaces as large as possible. Provide at least two access points to confined spaces. | Alan Speegle (Southern Co.)
417 | Space Layout | Civil | General Arrangement/Project Layout | Design | Safety | Rooms, walkways, platforms, etc. within a building which do not allow adequate egress or provide protection against hazardous materials can create safety hazards for construction workers. | Provide access by means of a ladder or stairway when there is a change in elevation of greater than 19 inches. | Alan Speegle (Southern Co.)
418 | Space Layout | Civil | General Arrangement/Project Layout | Design | Safety | Rooms, walkways, platforms, etc. within a building which do not allow adequate egress or provide protection against hazardous materials can create safety hazards for construction workers. | Establish survey control "permanantly" so that when structures are erected, survey control monuments are still accessible. | Alan Speegle (Southern Co.)
419 | Space Layout | Civil | General Arrangement/Project Layout | Design | Safety | Rooms, walkways, platforms, etc. within a building which do not allow adequate egress or provide protection against hazardous materials can create safety hazards for construction workers. | FGD General arrangement will provide enough space to lay the crane boom down during periods of high winds | Alan Speegle (Southern Co.)
420 | Stairs and Ramps | Civil | General Arrangement/Project Layout | Design | Safety | Stairs and ramps which are exposed to the weather and isolated can lead to fall hazards for construction workers. | Locate exterior stairs and ramps on the sheltered side of the structure to protect them from rain, snow, and ice. | Alan Speegle (Southern Co.)
421 | Stairs and Ramps | Civil | General Arrangement/Project Layout | Design | Safety | Stairs and ramps which are exposed to the weather and isolated can lead to fall hazards for construction workers. | Locate exterior stairs and ramps away from the north side of the structure to minimize the buildup of moss and ice. | Alan Speegle (Southern Co.)
422 | Stairs and Ramps | Civil | General Arrangement/Project Layout | Design | Safety | Stairs and ramps which are exposed to the weather and isolated can lead to fall hazards for construction workers. | Design stairs and ramps to run parallel and immediately adjacent to the structure, rather than perpendicular to the structure. | Alan Speegle (Southern Co.)
423 | Vehicular Traffic | Civil | General Arrangement/Project Layout | Design | Safety | Confined, congested, or sloped areas for contractor parking, material storage, and pedestrian access can lead to safety hazards for construction workers. | Do not locate constructor material lay-down areas next to or under electrical power lines. | Alan Speegle (Southern Co.)
424 | Vehicular Traffic | Civil | General Arrangement/Project Layout | Design | Safety | Confined, congested, or sloped areas for contractor parking, material storage, and pedestrian access can lead to safety hazards for construction workers. | Allow adequate room for constructor parking, temporary buildings, shops, material storage areas, and unobstructed access to and from the project site. | Alan Speegle (Southern Co.)
425 | Vehicular Traffic | Civil | General Arrangement/Project Layout | Design | Safety | Confined, congested, or sloped areas for contractor parking, material storage, and pedestrian access can lead to safety hazards for construction workers. | On sloped sites, orient the project layout or grade the site accordingly to minimize the amount of work on steep slopes. | Alan Speegle (Southern Co.)
426 | Vehicular Traffic | Civil | General Arrangement/Project Layout | Design | Safety | Confined, congested, or sloped areas for contractor parking, material storage, and pedestrian access can lead to safety hazards for construction workers. | Allow for pedestrian traffic to be isolated from construction vehicular traffic. | Alan Speegle (Southern Co.)
427 | Excavations | Civil | General Arrangement/Project Layout | Design | Safety | Inadequate clearance or congestion during excavation work can create cave-in and obstruction hazards for construction workers. | Allow adequate clearance for shoring, forms, equipment, and workers to perform below-grade work. | Alan Speegle (Southern Co.)
428 | Excavations | Civil | General Arrangement/Project Layout | Design | Safety | Inadequate clearance or congestion during excavation work can create cave-in and obstruction hazards for construction workers. | Locate new underground utilities and other below-grade features in areas easily accessible for excavation. Allow sufficient area around excavations for stockpiling the soil. | Alan Speegle (Southern Co.)
429 | Excavations | Civil | General Arrangement/Project Layout | Design | Safety | Inadequate clearance or congestion during excavation work can create cave-in and obstruction hazards for construction workers. | Avoid locating new utilities which cross under other pipelines, run directly adjacent to existing pipelines, intersect previously backfilled, disturbed, or fissured soil, intersect manhole excavations, or cross different types or conditions of soil. | Alan Speegle (Southern Co.)
430 | Excavations | Civil | General Arrangement/Project Layout | Design | Safety | Inadequate clearance or congestion during excavation work can create cave-in and obstruction hazards for construction workers. | Consider area drainage of excavations during construction when developing the plot plan. | Alan Speegle (Southern Co.)
431 | Openings | Civil | General Arrangement/Project Layout | Design | Safety | General Arrangement/Project Layout: Openings | Locate roof openings away from the edge of the structure. | Alan Speegle (Southern Co.)
432 | Openings | Civil | General Arrangement/Project Layout | Design | Safety | General Arrangement/Project Layout: Openings | Group roof openings together to create one larger opening rather than many smaller openings. | Alan Speegle (Southern Co.)
433 | Openings | Civil | General Arrangement/Project Layout | Design | Safety | General Arrangement/Project Layout: Openings | Eliminate tripping hazards around roof openings. | Alan Speegle (Southern Co.)
434 | Openings | Civil | General Arrangement/Project Layout | Design | Safety | General Arrangement/Project Layout: Openings | Locate rooftop mechanical/HVAC equipment away from roof openings. | Alan Speegle (Southern Co.)
435 | Road Design | Civil | Roads And Parking | Design | Safety | Inadequate or congested traffic areas, and unstable road edges and shoulders, can lead to safety hazards for construction workers. | In embankments directly adjacent to the road edge, provide an initial bench at the road grade to provide room for crews to work. | Alan Speegle (Southern Co.)
436 | Road Design | Civil | Roads And Parking | Design | Safety | Inadequate or congested traffic areas, and unstable road edges and shoulders, can lead to safety hazards for construction workers. | Provide structural support at the edge of roadways to keep heavy construction equipment from crushing the edge and overturning. | Alan Speegle (Southern Co.)
437 | Road Design | Civil | Roads And Parking | Design | Safety | Inadequate or congested traffic areas, and unstable road edges and shoulders, can lead to safety hazards for construction workers. | Provide a smooth transition between the road and shoulder. | Alan Speegle (Southern Co.)
438 | Road Design | Civil | Roads And Parking | Design | Safety | Inadequate or congested traffic areas, and unstable road edges and shoulders, can lead to safety hazards for construction workers. | Design the slope, width, height, turning radius, and surface treatment of traffic surfaces with consideration of the anticipated size, weight, and maneuverability of the construction equipment. | Alan Speegle (Southern Co.)
439 | Road Design | Civil | Roads And Parking | Design | Safety | Inadequate or congested traffic areas, and unstable road edges and shoulders, can lead to safety hazards for construction workers. | Design traffic barriers and guardrails so that there is no need to temporarily or permanently replace or re-design them when new pavement overlays are put down. | Alan Speegle (Southern Co.)
440 | Road Design | Civil | Roads And Parking | Design | Safety | Inadequate or congested traffic areas, and unstable road edges and shoulders, can lead to safety hazards for construction workers. | Locate project control points away from areas of high construction. | Alan Speegle (Southern Co.)
441 | Road Design | Civil | Roads And Parking | Design | Safety | Inadequate or congested traffic areas, and unstable road edges and shoulders, can lead to safety hazards for construction workers. | Guard posts are required to protect steel bents and structures from trucks or loaders in vehicle access areas. | Alan Speegle (Southern Co.)
442 | Road Design | Civil | Roads And Parking | Design | Safety | Inadequate or congested traffic areas, and unstable road edges and shoulders, can lead to safety hazards for construction workers. | Guard posts are required to protect equipment adjacent to vehicle access areas. | Alan Speegle (Southern Co.)
443 | Schedule/Sequence | Civil | Roads And Parking | Design | Safety | Road construction, maintenance, and excavation operations can be hazardous for construction workers when working around existing utilities and ongoing public traffic. | Require hand excavation around existing underground utilities. | Alan Speegle (Southern Co.)
444 | Schedule/Sequence | Civil | Roads And Parking | Design | Safety | Road construction, maintenance, and excavation operations can be hazardous for construction workers when working around existing utilities and ongoing public traffic. | Design new utilities under roadways and sidewalks to be placed using trenchless technologies or tunneling instead of trenching. | Alan Speegle (Southern Co.)
445 | Parking | Civil | Roads And Parking | Design | Safety | The project schedule and work sequence can lead to safety hazards for construction workers. | Design and schedule new parking areas to be constructed as early as possible to provide a formal, safe location for workers to store materials and equipment. | Alan Speegle (Southern Co.)
446 | Parking | Civil | Roads And Parking | Design | Safety | The project schedule and work sequence can lead to safety hazards for construction workers. | Prior to the start of the project, erect informational signs near the project. | Alan Speegle (Southern Co.)
447 | Parking | Civil | Roads And Parking | Design | Safety | The project schedule and work sequence can lead to safety hazards for construction workers. | Use a slope of 1/8" per foot minimum to prevent water ponding. | Alan Speegle (Southern Co.)
448 | Ladders | Civil | Stairs, Ladder, Ramp | Design | Safety | The orientation and design of ladders with respect to the structure can create fall hazards for construction workers. | Design ladders to be vertical, or not exceeding 15 degrees forward, and straight throughout their length. | Alan Speegle (Southern Co.)
449 | Ladders | Civil | Stairs, Ladder, Ramp | Design | Safety | The orientation and design of ladders with respect to the structure can create fall hazards for construction workers. | Orient ladders such that the person faces the structure while climbing. | Alan Speegle (Southern Co.)
450 | Ladders | Civil | Stairs, Ladder, Ramp | Design | Safety | The orientation and design of ladders with respect to the structure can create fall hazards for construction workers. | Provide safety gates at the top of walk through and side access ladders. | Alan Speegle (Southern Co.)
451 | Ladders | Civil | Stairs, Ladder, Ramp | Design | Safety | The orientation and design of ladders with respect to the structure can create fall hazards for construction workers. | Provide a minimum 2'-6" x 2'-6" landing area at the top and bottom of ladders. Coordinate the layout of the landings with the structure design to eliminate tripping hazards. | Alan Speegle (Southern Co.)
452 | Ladders | Civil | Stairs, Ladder, Ramp | Design | Safety | The orientation and design of ladders with respect to the structure can create fall hazards for construction workers. | Design the step-across distance between the center of the step/rung and the nearest edge of a landing to be between 7 and 12 inches. Provide a landing platform if more than 12 inches. | Alan Speegle (Southern Co.)
453 | Ladders | Civil | Stairs, Ladder, Ramp | Design | Safety | The orientation and design of ladders with respect to the structure can create fall hazards for construction workers. | For walk-through-ladder extensions, omit steps/rungs within the extension. Provide between 24 and 30 inches clearance between the side rails. | Alan Speegle (Southern Co.)
454 | Ladders | Civil | Stairs, Ladder, Ramp | Design | Safety | The orientation and design of ladders with respect to the structure can create fall hazards for construction workers. | Design the side rails and rungs of step-through ladders to extend at least 42 inches above the floor or landing platform. Side-access ladders rails and rungs shall extend 4'-0" above the floor or platform. | Alan Speegle (Southern Co.)
455 | Ladder - Rungs | Civil | Stairs, Ladder, Ramp | Design | Safety | Ladder step or rung size, spacing, and materials can make ladders awkward to climb or slippery and create fall hazards for construction workers. | Design ladder steps/rungs to be spaced between 11 and 12 inches apart, parallel, level, and uniformly spaced throughout the ladder. | Alan Speegle (Southern Co.)
456 | Ladder - Rungs | Civil | Stairs, Ladder, Ramp | Design | Safety | Ladder step or rung size, spacing, and materials can make ladders awkward to climb or slippery and create fall hazards for construction workers. | Locate the first step/rung between 6 and 12 inches above the bottom landing, and the top step/rung at the level of the top landing. | Alan Speegle (Southern Co.)
457 | Ladder - Rungs | Civil | Stairs, Ladder, Ramp | Design | Safety | Ladder step or rung size, spacing, and materials can make ladders awkward to climb or slippery and create fall hazards for construction workers. | Design the ladder steps/rungs of individual step/rung ladders to be shaped to prevent slipping off the end of the steps/rungs. | Alan Speegle (Southern Co.)
458 | Ladder - Caged | Civil | Stairs, Ladder, Ramp | Design | Safety | Inadequately designed ladder cages can create obstructions or snag construction worker clothing or equipment while climbing, and lead to construction workers falling. | Design horizontal bands to be fastened to the side rails of rail ladders, or directly to the structure for individual-rung ladders. | Alan Speegle (Southern Co.)
459 | Ladder - Caged | Civil | Stairs, Ladder, Ramp | Design | Safety | Inadequately designed ladder cages can create obstructions or snag construction worker clothing or equipment while climbing, and lead to construction workers falling. | Design vertical bars to be on the inside of the horizontal bands and fastened to them. | Alan Speegle (Southern Co.)
460 | Ladder - Caged | Civil | Stairs, Ladder, Ramp | Design | Safety | Inadequately designed ladder cages can create obstructions or snag construction worker clothing or equipment while climbing, and lead to construction workers falling. | Design horizontal bands to be spaced at intervals not more than 4 ft. apart between centerlines. | Alan Speegle (Southern Co.)
461 | Ladder - Caged | Civil | Stairs, Ladder, Ramp | Design | Safety | Inadequately designed ladder cages can create obstructions or snag construction worker clothing or equipment while climbing, and lead to construction workers falling. | Design vertical bars to be spaced at intervals not more than 9.5 in. apart between centerlines. | Alan Speegle (Southern Co.)
462 | Ladder - Caged | Civil | Stairs, Ladder, Ramp | Design | Safety | Inadequately designed ladder cages can create obstructions or snag construction worker clothing or equipment while climbing, and lead to construction workers falling. | Keep the inside of the cage clear of projections. | Alan Speegle (Southern Co.)
463 | Ladder - Cage Dimensions | Civil | Stairs, Ladder, Ramp | Design | Safety | Ladder cages can create fall hazards for construction workers if they are too small, too large, or do not provide protection along the entire length of the ladder. | Design cages to extend at least 27 inches, but not more than 30 inches, from the centerline of the step or rung, and not less than 27 inches wide. | Alan Speegle (Southern Co.)
464 | Ladder - Cage Dimensions | Civil | Stairs, Ladder, Ramp | Design | Safety | Ladder cages can create fall hazards for construction workers if they are too small, too large, or do not provide protection along the entire length of the ladder. | Design the bottom of the cage to be between 7 and 8 feet above the point of access to the bottom of the ladder. Flare the bottom of the cage not less than 4 inches between the bottom horizontal band and the next higher band. | Alan Speegle (Southern Co.)
465 | Ladder - Cage Dimensions | Civil | Stairs, Ladder, Ramp | Design | Safety | Ladder cages can create fall hazards for construction workers if they are too small, too large, or do not provide protection along the entire length of the ladder. | Design the top edge of the step-through cage ladder to be a minimum of 42 inches above the top of the platform, or the point of access at the top of the ladder. Design the top edge of the side access ladder cage to be a minimum of 48' above the top of th | Alan Speegle (Southern Co.)
466 | Ladder - Length | Civil | Stairs, Ladder, Ramp | Design | Safety | Ladder lengths can affect a construction worker's risk of falling if the ladders are long and do not provide a rest area, or if they do not extend above the top landing. | Provide ladder cages, wells, or other safety devices where the length of climb is less than 30 feet but the top of the ladder is at a distance greater than 30 feet above lower levels. | Alan Speegle (Southern Co.)
467 | Ladder - Length | Civil | Stairs, Ladder, Ramp | Design | Safety | Ladder lengths can affect a construction worker's risk of falling if the ladders are long and do not provide a rest area, or if they do not extend above the top landing. | If the total length of a climb equals or exceeds 20 feet, provide a cage or well, and multiple ladder sections, each section not to exceed 30 feet. Offset each ladder section from adjacent sections, and provide landing platforms at intervals of 30 feet m | Alan Speegle (Southern Co.)
468 | Ladder - Clearance | Civil | Stairs, Ladder, Ramp | Design | Safety | Ladders which have attachments or other objects adjacent to the climbing area can obstruct workers during climbing and create a fall hazard. | Design ladders to prevent injury from punctures or lacerations, and prevent snagging of clothing. | Alan Speegle (Southern Co.)
469 | Ladder - Clearance | Civil | Stairs, Ladder, Ramp | Design | Safety | Ladders which have attachments or other objects adjacent to the climbing area can obstruct workers during climbing and create a fall hazard. | Provide a minimum perpendicular clearance of 7 inches between ladder rungs, cleats, or steps, and any obstruction behind the ladder, except that the clearance for elevator pit ladders may be no less than 4.5 inches. | Alan Speegle (Southern Co.)
470 | Ladder - Clearance | Civil | Stairs, Ladder, Ramp | Design | Safety | Ladders which have attachments or other objects adjacent to the climbing area can obstruct workers during climbing and create a fall hazard. | Provide a minimum perpendicular clearance of 30 inches between the centerline of ladder rungs, cleats, or steps, and any obstruction on the climbing side of the ladder. If obstructions are unavoidable, clearance may be reduced to 24 inches provided a def | Alan Speegle (Southern Co.)
471 | Ladder - Loads | Civil | Stairs, Ladder, Ramp | Design | Safety | Ladders which are not designed to withstand construction loading can collapse and lead to construction workers falling. | Design ladders to be capable of supporting at least two loads of 200 lbs. each concentrated between any two consecutive attachments. | Alan Speegle (Southern Co.)
472 | Ladder - Loads | Civil | Stairs, Ladder, Ramp | Design | Safety | Ladders which are not designed to withstand construction loading can collapse and lead to construction workers falling. | Design each step or rung to be capable of supporting a load of at least 200 lbs. applied in the middle of the step or rung. | Alan Speegle (Southern Co.)
473 | Ladder - Loads | Civil | Stairs, Ladder, Ramp | Design | Safety | Ladders which are not designed to withstand construction loading can collapse and lead to construction workers falling. | Design ladders for any anticipated loads caused by ice buildup, wind, rigging, and impact loads resulting from the use of ladder safety devices. | Alan Speegle (Southern Co.)
474 | Ladders vs Stairs | Civil | Stairs, Ladder, Ramp | Design | Safety | Frequent use of ladders by construction and maintenance workers to move material and equipment increases the possibility of falling from the ladders. | Consider stairs in lieu of a ladder when the ladder will be used frequently to move material and equipment. | Alan Speegle (Southern Co.)
475 | Ramps | Civil | Stairs, Ladder, Ramp | Design | Safety | Ramps which do not contain any slip resistance measures or are subject to water, snow, or ice can be a falling hazard for construction workers. | Provide a non-slip surface treatment on ramps to help prevent slipping. | Alan Speegle (Southern Co.)
476 | Ramps | Civil | Stairs, Ladder, Ramp | Design | Safety | Ramps which do not contain any slip resistance measures or are subject to water, snow, or ice can be a falling hazard for construction workers. | Provide cleats on steel or wood ramps, or create grooves on concrete ramps, to help prevent slipping. | Alan Speegle (Southern Co.)
477 | Ramps | Civil | Stairs, Ladder, Ramp | Design | Safety | Ramps which do not contain any slip resistance measures or are subject to water, snow, or ice can be a falling hazard for construction workers. | In areas which receive snow, provide a covering, overhang, or extend the roof line over exterior ramps. | Alan Speegle (Southern Co.)
478 | Ramps | Civil | Stairs, Ladder, Ramp | Design | Safety | Ramps which do not contain any slip resistance measures or are subject to water, snow, or ice can be a falling hazard for construction workers. | Use a maximum ramp slope of 7 degrees. | Alan Speegle (Southern Co.)
479 | Stairs | Civil | Stairs, Ladder, Ramp | Design | Safety | A lack of uniform stairway slopes and stair dimensions throughout a project can lead to construction workers tripping or falling due to unanticipated stairway layouts. | Maintain a uniform stair slope throughout the project. | Alan Speegle (Southern Co.)
480 | Stairs | Civil | Stairs, Ladder, Ramp | Design | Safety | A lack of uniform stairway slopes and stair dimensions throughout a project can lead to construction workers tripping or falling due to unanticipated stairway layouts. | Use consistent tread and riser dimensions that meet code requirements throughout the stairway run and the project. | Alan Speegle (Southern Co.)
481 | Stairs | Civil | Stairs, Ladder, Ramp | Design | Safety | A lack of uniform stairway slopes and stair dimensions throughout a project can lead to construction workers tripping or falling due to unanticipated stairway layouts. | Establish survey control "permanently" so that when structures are erected, survey control monuments are still accessible. | Alan Speegle (Southern Co.)
482 | Stair Landings | Civil | Stairs, Ladder, Ramp | Design | Safety | Inadequate, misplaced, or obstructed stairway landings can lead to falls when stepping onto or off of a stairway. | Coordinate the layout of exterior stair landings with the foundation design to provide a smooth, clear landing area free of tripping hazards. | Alan Speegle (Southern Co.)
483 | Stair Landings | Civil | Stairs, Ladder, Ramp | Design | Safety | Inadequate, misplaced, or obstructed stairway landings can lead to falls when stepping onto or off of a stairway. | Avoid stair landings constructed separate from the stairs. | Alan Speegle (Southern Co.)
484 | Stair Landings | Civil | Stairs, Ladder, Ramp | Design | Safety | Inadequate, misplaced, or obstructed stairway landings can lead to falls when stepping onto or off of a stairway. | Provide a minimum 2'-6" x 2'-6" landing area. | Alan Speegle (Southern Co.)
485 | Stair Landings | Civil | Stairs, Ladder, Ramp | Design | Safety | Inadequate, misplaced, or obstructed stairway landings can lead to falls when stepping onto or off of a stairway. | Build stair landings up above an uneven grade. | Alan Speegle (Southern Co.)
486 | Stair Materials | Civil | Stairs, Ladder, Ramp | Design | Safety | Stairway materials should be selected with consideration of the anticipated construction work area and surrounding environmental conditions to minimize deterioration of the stairways and the possibility of falling. | Use perforated steel or steel grating for stair treads on exterior stairways to prevent slipping, or when there is a need to "see through" the stairs in tight, congested work areas. | Alan Speegle (Southern Co.)
487 | Stair Materials | Civil | Stairs, Ladder, Ramp | Design | Safety | Stairway materials should be selected with consideration of the anticipated construction work area and surrounding environmental conditions to minimize deterioration of the stairways and the possibility of falling. | Consider using prefabricated or ground-assembled stairways which can be erected as one assembly. | Alan Speegle (Southern Co.)
488 | Stair Materials | Civil | Stairs, Ladder, Ramp | Design | Safety | Stairway materials should be selected with consideration of the anticipated construction work area and surrounding environmental conditions to minimize deterioration of the stairways and the possibility of falling. | Use steel or concrete for stairways in areas where welding or other potential fire sources are present. | Alan Speegle (Southern Co.)
489 | Stair Materials | Civil | Stairs, Ladder, Ramp | Design | Safety | Stairway materials should be selected with consideration of the anticipated construction work area and surrounding environmental conditions to minimize deterioration of the stairways and the possibility of falling. | Use concrete or other nonconductive materials instead of steel for stairways in areas where electrical work will be performed. | Alan Speegle (Southern Co.)
490 | Stair Location | Civil | Stairs, Ladder, Ramp | Design | Safety | Exposed or narrow stairways can create climbing problems for construction workers carrying materials or equipment and lead to falls. | Design exterior stairs to be directly adjacent and parallel, rather than perpendicular, to the structure. | Alan Speegle (Southern Co.)
491 | Stair Location | Civil | Stairs, Ladder, Ramp | Design | Safety | Exposed or narrow stairways can create climbing problems for construction workers carrying materials or equipment and lead to falls. | Design circumferential stairways to ascend clockwise. | Alan Speegle (Southern Co.)
492 | Stair Location | Civil | Stairs, Ladder, Ramp | Design | Safety | Exposed or narrow stairways can create climbing problems for construction workers carrying materials or equipment and lead to falls. | Place exterior stairs on the sunny side of the structure to prevent the buildup of ice. | Alan Speegle (Southern Co.)
493 | Stair Railing | Civil | Stairs, Ladder, Ramp | Design | Safety | Stairways with inadequate or non-existent handrails or stairrails can create fall hazards for construction workers. | Provide at least one handrail or railing along stairways with 4 or more risers, or which rise more than 30 inches in height, whichever is less. | Alan Speegle (Southern Co.)
494 | Stair Erection | Civil | Stairs, Ladder, Ramp | Design | Safety | To get to elevated work areas prior to erection of permanent stairways, construction workers must use temporary stairways, ladders, or manlifts which are often unstable, inadequately designed, or damaged. | Design and schedule permanent stairways to be built as soon as possible in the construction phase and used by the construction workers. | Alan Speegle (Southern Co.)
495 | Steel Beam, Purlins, Girts, Utility Bridge, Bent form Plate | Civil | Structural Steel Framing | Design | Safety | Hazzards associated with steel erection can be reduced or eliminated by following the requirements on OSHA 1926 Subpart R. | Steel member marking and tagging procedure should be described in our purchase order documents. This can become complicated for hot dipped galvanized projects. See what construction services representive wants for the marking and tagging. | Alan Speegle (Southern Co.)
496 | Steel Beam, Purlins, Girts, Utility Bridge, Bent form Plate | Civil | Structural Steel Framing | Design | Safety | Hazzards associated with steel erection can be reduced or eliminated by following the requirements on OSHA 1926 Subpart R. | Consider the erection process when designing steel connections. | Alan Speegle (Southern Co.)
497 | Steel Beam, Purlins, Girts, Utility Bridge, Bent form Plate | Civil | Structural Steel Framing | Design | Safety | Hazzards associated with steel erection can be reduced or eliminated by following the requirements on OSHA 1926 Subpart R. | Design beam-to-column double-connections to have full support for the beams during the connection process. | Alan Speegle (Southern Co.)
498 | Steel Beam, Purlins, Girts, Utility Bridge, Bent form Plate | Civil | Structural Steel Framing | Design | Safety | Hazzards associated with steel erection can be reduced or eliminated by following the requirements on OSHA 1926 Subpart R. | Design a fix for steel beams of common depth connecting into the column web at the same location. | Alan Speegle (Southern Co.)
499 | Steel Beam, Purlins, Girts, Utility Bridge, Bent form Plate | Civil | Structural Steel Framing | Design | Safety | Hazzards associated with steel erection can be reduced or eliminated by following the requirements on OSHA 1926 Subpart R. | Provide pin-hole or bolted connections on beams and columns to create proper alignment and stability immediately after placement of the members. | Alan Speegle (Southern Co.)
500 | Steel Beam, Purlins, Girts, Utility Bridge, Bent form Plate | Civil | Structural Steel Framing | Design | Safety | Hazzards associated with steel erection can be reduced or eliminated by following the requirements on OSHA 1926 Subpart R. | Erection drawing, bolt list, and fasteners must be delivered prior to/or with the delivery of the fabricated steel. | Alan Speegle (Southern Co.)
501 | Steel Beam, Purlins, Girts, Utility Bridge, Bent form Plate | Civil | Structural Steel Framing | Design | Safety | Hazzards associated with steel erection can be reduced or eliminated by following the requirements on OSHA 1926 Subpart R. | Discuss with construction services representatives the need to provide holes in the webs of beams above piping for attachment of supports and lifelines. | Alan Speegle (Southern Co.)
502 | Steel Beam, Purlins, Girts, Utility Bridge, Bent form Plate | Civil | Structural Steel Framing | Design | Safety | Hazzards associated with steel erection can be reduced or eliminated by following the requirements on OSHA 1926 Subpart R. | Design roof to support construction equipment and scaffolding used to install insulation and siding. | Alan Speegle (Southern Co.)
503 | Steel Beam, Purlins, Girts, Utility Bridge, Bent form Plate | Civil | Structural Steel Framing | Design | Safety | Hazzards associated with steel erection can be reduced or eliminated by following the requirements on OSHA 1926 Subpart R. | Use steel pre-fabricated or ground-assembled members for work over diked areas, water, railways, roads, etc. | Alan Speegle (Southern Co.)
504 | Steel Beam, Purlins, Girts, Utility Bridge, Bent form Plate | Civil | Structural Steel Framing | Design | Safety | Hazzards associated with steel erection can be reduced or eliminated by following the requirements on OSHA 1926 Subpart R. | Spec for Structural Joints Using ASTM A325 Bolts (pretensioned) requires at least 3 bolts of each diameter, length and grade (along with flat hardened washer and nut) to be checked at the job site in a device capable of indicating bolt tension. Structura | Alan Speegle (Southern Co.)
505 | Steel Beam, Purlins, Girts, Utility Bridge, Bent form Plate | Civil | Structural Steel Framing | Design | Safety | Hazzards associated with steel erection can be reduced or eliminated by following the requirements on OSHA 1926 Subpart R. | Discuss with construction services representative if our engineers needs to design a method of attaching temporary railing and safety lines for construction workers. | Alan Speegle (Southern Co.)
506 | Steel Beam, Purlins, Girts, Utility Bridge, Bent form Plate | Civil | Structural Steel Framing | Design | Safety | Hazzards associated with steel erection can be reduced or eliminated by following the requirements on OSHA 1926 Subpart R. | Consider using composite beams to support elevated concrete floors. | Alan Speegle (Southern Co.)
507 | Steel Beam, Purlins, Girts, Utility Bridge, Bent form Plate | Civil | Structural Steel Framing | Design | Safety | Hazzards associated with steel erection can be reduced or eliminated by following the requirements on OSHA 1926 Subpart R. | If the utility bridge steel is needed early consider a typical bay spacing, bent design, and bridge or truss design. Consider framing trussed into column flanges. | Alan Speegle (Southern Co.)
508 | Steel Beam, Purlins, Girts, Utility Bridge, Bent form Plate | Civil | Structural Steel Framing | Design | Safety | Hazzards associated with steel erection can be reduced or eliminated by following the requirements on OSHA 1926 Subpart R. | Discuss with construction services representatives if the structural drawings, shop fabrication drawings, and fabricated steel, should make provisions for attaching field safety appurtenaces. Example: Utility bridge and truss make want to have holes for | Alan Speegle (Southern Co.)
509 | Steel Beam, Purlins, Girts, Utility Bridge, Bent form Plate | Civil | Structural Steel Framing | Design | Safety | Hazzards associated with steel erection can be reduced or eliminated by following the requirements on OSHA 1926 Subpart R. | Maximize the use of field bolted joints (instead of field welded joints) to expedite erection. | Alan Speegle (Southern Co.)
510 | Steel Beam, Purlins, Girts, Utility Bridge, Bent form Plate | Civil | Structural Steel Framing | Design | Safety | Hazzards associated with steel erection can be reduced or eliminated by following the requirements on OSHA 1926 Subpart R. | Identify shop assembled items. Consider using modular shop welded frames and platform sections to reduce erection time. | Alan Speegle (Southern Co.)
511 | Steel Beam, Purlins, Girts, Utility Bridge, Bent form Plate | Civil | Structural Steel Framing | Design | Safety | Hazzards associated with steel erection can be reduced or eliminated by following the requirements on OSHA 1926 Subpart R. | (For unit price steel fabrication contracts) Determine the fabricator's commitment to deliver steel. Is the fabircator: flexible to shift the steel deliver schedule; increase the scope of work; decrease the scope of work; sublet work; or work overtime. | Alan Speegle (Southern Co.)
512 | Steel Beam, Purlins, Girts, Utility Bridge, Bent form Plate | Civil | Structural Steel Framing | Design | Safety | Hazzards associated with steel erection can be reduced or eliminated by following the requirements on OSHA 1926 Subpart R. | Consider who furnishes concrete metal form deck placing drawings, deck, closure pieces, and fasteners. Who install these items. | Alan Speegle (Southern Co.)
513 | Steel Beam, Purlins, Girts, Utility Bridge, Bent form Plate | Civil | Structural Steel Framing | Design | Safety | Hazzards associated with steel erection can be reduced or eliminated by following the requirements on OSHA 1926 Subpart R. | If concrete edge form deck is used, determine: who provides and install; if welded or bolted; if ground assembled or in the air; and if plate will be held 2' short to allow the iron worker to bolt up the beam to column connection. | Alan Speegle (Southern Co.)
514 | Steel Beam, Purlins, Girts, Utility Bridge, Bent form Plate | Civil | Structural Steel Framing | Design | Safety | Hazzards associated with steel erection can be reduced or eliminated by following the requirements on OSHA 1926 Subpart R. | Determine is MTO, material take-off, pay categories will be shown on the steel shop drawings. | Alan Speegle (Southern Co.)
515 | Steel Beam, Purlins, Girts, Utility Bridge, Bent form Plate | Civil | Structural Steel Framing | Design | Safety | Hazzards associated with steel erection can be reduced or eliminated by following the requirements on OSHA 1926 Subpart R. | Design pipe bridges to maintain adequate clearances for construction equipment and cranes. | Alan Speegle (Southern Co.)
516 | Steel Beam, Purlins, Girts, Utility Bridge, Bent form Plate | Civil | Structural Steel Framing | Design | Safety | Hazzards associated with steel erection can be reduced or eliminated by following the requirements on OSHA 1926 Subpart R. | The steel inquiry documents should consider these items: tolerances, need for fabricator's representative in the field; basis for change order, shipping weights (with out material waste), touch up paint, erector should verify top of piers and anchor bolt | Alan Speegle (Southern Co.)
517 | Steel Beam, Purlins, Girts, Utility Bridge, Bent form Plate | Civil | Structural Steel Framing | Design | Safety | Hazzards associated with steel erection can be reduced or eliminated by following the requirements on OSHA 1926 Subpart R. | Steel drawings and specifications allow or encourage ground assembly of utility bridges, flue duct bents and towers. For example, the utility bridge 60-foot trusses could be ground assembled. Then the pipe and cable tray members could be added before th | Alan Speegle (Southern Co.)
518 | Steel Beam, Purlins, Girts, Utility Bridge, Bent form Plate | Civil | Structural Steel Framing | Design | Safety | Hazzards associated with steel erection can be reduced or eliminated by following the requirements on OSHA 1926 Subpart R. | The flue gas duct work and/or duct support steel will be designed for construction loads associated with the installation of walk boards and support brackets for construction workers. | Alan Speegle (Southern Co.)
519 | Steel Column & Vertical Bracing | Civil; Mechanical | Structural Steel Framing | Design | Safety | Tall steel structures can easily collapse during the erection process if the steel is not adequately supported before it is permanently bolted or welded into place. | Limit the lift heights of steel erection. | Alan Speegle (Southern Co.)
520 | Steel Column & Vertical Bracing | Civil | Structural Steel Framing | Design | Safety | Tall steel structures can easily collapse during the erection process if the steel is not adequately supported before it is permanently bolted or welded into place. | Ask construction services representive if columns should be provided with holes at 21 and 42 inches above the floor level to provide support locations for lifelines and guardrails. Consider impact of column splice on these holes. | Alan Speegle (Southern Co.)
521 | Steel Column & Vertical Bracing | Civil | Structural Steel Framing | Design | Safety | Tall steel structures can easily collapse during the erection process if the steel is not adequately supported before it is permanently bolted or welded into place. | Locate column splices between 2 and 4 feet above the finished floor level, and at two-story intervals. See the Technical Lead - Structural Steel for recommended column splice locations and maximun lenghts of columns. | Alan Speegle (Southern Co.)
522 | Steel Column & Vertical Bracing | Civil | Structural Steel Framing | Design | Safety | Tall steel structures can easily collapse during the erection process if the steel is not adequately supported before it is permanently bolted or welded into place. | All columns shall be anchored by a minimum of 4 anchor rods (anchor bolts). | Alan Speegle (Southern Co.)
523 | Steel Column & Vertical Bracing | Civil | Structural Steel Framing | Design | Safety | Tall steel structures can easily collapse during the erection process if the steel is not adequately supported before it is permanently bolted or welded into place. | Anchor bolts shall not be repaired, replaced, or field-modified without approval of the structural engineer of record. | Alan Speegle (Southern Co.)
524 | Steel Column & Vertical Bracing | Civil | Structural Steel Framing | Design | Safety | Tall steel structures can easily collapse during the erection process if the steel is not adequately supported before it is permanently bolted or welded into place. | In multi-story structures, when holes in the column web are used for perimeter safety cables, the column splice must be placed sufficiently high so as not to interfere with any attachments to the column necessary for the column splice. | Alan Speegle (Southern Co.)
525 | Steel Column & Vertical Bracing | Civil | Structural Steel Framing | Design | Safety | Tall steel structures can easily collapse during the erection process if the steel is not adequately supported before it is permanently bolted or welded into place. | Decide who will provide shims below base plates. Decide if shim will be left in place after the grout in installed. | Alan Speegle (Southern Co.)
526 | Steel Column & Vertical Bracing | Civil | Structural Steel Framing | Design | Safety | Tall steel structures can easily collapse during the erection process if the steel is not adequately supported before it is permanently bolted or welded into place. | Decide which base plate will be shipped loose and which will be shop welded. | Alan Speegle (Southern Co.)
527 | Steel Column & Vertical Bracing | Civil | Structural Steel Framing | Design | Safety | Tall steel structures can easily collapse during the erection process if the steel is not adequately supported before it is permanently bolted or welded into place. | Try to minimize the horizontal struts and vertical bracing in areas where construction and operation personnel will need access. | Alan Speegle (Southern Co.)
528 | Steel Column & Vertical Bracing | Civil | Structural Steel Framing | Design | Safety | Tall steel structures can easily collapse during the erection process if the steel is not adequately supported before it is permanently bolted or welded into place. | Structural steel fabrication and erection shall meet the requirement of Code of Standard Practice of Steel Buildings and Bridges March 7, 2000. | Alan Speegle (Southern Co.)
529 | High Strength Bolts | Civil | Structural Steel Framing | Design | Safety | Complicated or non-standard connections can lead to confusion and mis-installation of bolts and washers. | Bolts should have the same diameter, finish, tension requirements, washer, same ASTM designation, connection type (N or X threads in shear plane), and installation method. | Alan Speegle (Southern Co.)
530 | High Strength Bolts | Civil | Structural Steel Framing | Design | Safety | Complicated or non-standard connections can lead to confusion and mis-installation of bolts and washers. | Consider using a "Squirter DTI" (Direct Tension Indicators) if pretensioned high-strength bolts are a requirement. | Alan Speegle (Southern Co.)
531 | Miscellaneous Steel, Railing and Grating | Civil | Structural Steel Framing | Design | Safety | Structural steel erection operations can lead to collapse if adequate support is not provided for the members before permanent connection. Welding operations can create fire hazards due to excessive slag or sparks, and also expose construction workers to | Design the structural members to withstand all anticipated construction loading during fabrication, storage, erection, and final connection. | Alan Speegle (Southern Co.)
532 | Miscellaneous Steel, Railing and Grating | Civil | Structural Steel Framing | Design | Safety | Structural steel erection operations can lead to collapse if adequate support is not provided for the members before permanent connection. Welding operations can create fire hazards due to excessive slag or sparks, and also expose construction workers to | Design member depths to allow adequate head room clearance around stairs, platforms, valves, and all areas of egress. | Alan Speegle (Southern Co.)
533 | Miscellaneous Steel, Railing and Grating | Civil | Structural Steel Framing | Design | Safety | Structural steel erection operations can lead to collapse if adequate support is not provided for the members before permanent connection. Welding operations can create fire hazards due to excessive slag or sparks, and also expose construction workers to | Minimize the amount of overhead work. | Alan Speegle (Southern Co.)
534 | Miscellaneous Steel, Railing and Grating | Civil | Structural Steel Framing | Design | Safety | Structural steel erection operations can lead to collapse if adequate support is not provided for the members before permanent connection. Welding operations can create fire hazards due to excessive slag or sparks, and also expose construction workers to | Design members which are of consistent size, light weight, and easy to handle. | Alan Speegle (Southern Co.)
535 | Miscellaneous Steel, Railing and Grating | Civil | Structural Steel Framing | Design | Safety | Structural steel erection operations can lead to collapse if adequate support is not provided for the members before permanent connection. Welding operations can create fire hazards due to excessive slag or sparks, and also expose construction workers to | Limit lift heights for steel columns. | Alan Speegle (Southern Co.)
536 | Miscellaneous Steel, Railing and Grating | Civil | Structural Steel Framing | Design | Safety | Structural steel erection operations can lead to collapse if adequate support is not provided for the members before permanent connection. Welding operations can create fire hazards due to excessive slag or sparks, and also expose construction workers to | Design connections to be bolted or welded in the shop rather than in the field. | Alan Speegle (Southern Co.)
537 | Miscellaneous Steel, Railing and Grating | Civil | Structural Steel Framing | Design | Safety | Structural steel erection operations can lead to collapse if adequate support is not provided for the members before permanent connection. Welding operations can create fire hazards due to excessive slag or sparks, and also expose construction workers to | Minimize field welding of steel with a galvanized coating. | Alan Speegle (Southern Co.)
538 | Miscellaneous Steel, Railing and Grating | Civil | Structural Steel Framing | Design | Safety | Structural steel erection operations can lead to collapse if adequate support is not provided for the members before permanent connection. Welding operations can create fire hazards due to excessive slag or sparks, and also expose construction workers to | Ensure that the welding procedures specified are compatible with the materials being welded. | Alan Speegle (Southern Co.)
539 | Miscellaneous Steel, Railing and Grating | Civil | Structural Steel Framing | Design | Safety | Structural steel erection operations can lead to collapse if adequate support is not provided for the members before permanent connection. Welding operations can create fire hazards due to excessive slag or sparks, and also expose construction workers to | Roof steel shall be designed for fall protection anchorage points. | Alan Speegle (Southern Co.)
540 | Miscellaneous Steel, Railing and Grating | Civil | Structural Steel Framing | Design | Safety | Structural steel erection operations can lead to collapse if adequate support is not provided for the members before permanent connection. Welding operations can create fire hazards due to excessive slag or sparks, and also expose construction workers to | Drawings and specifications for steel should meet the current codes and standards. | Alan Speegle (Southern Co.)
541 | Miscellaneous Steel, Railing and Grating | Civil | Structural Steel Framing | Design | Safety | Structural steel erection operations can lead to collapse if adequate support is not provided for the members before permanent connection. Welding operations can create fire hazards due to excessive slag or sparks, and also expose construction workers to | Engineer's stamp is required on all engineering drawings and specifications generated by outside companies. | Alan Speegle (Southern Co.)
542 | Miscellaneous Steel, Railing and Grating | Civil | Structural Steel Framing | Design | Safety | Structural steel erection operations can lead to collapse if adequate support is not provided for the members before permanent connection. Welding operations can create fire hazards due to excessive slag or sparks, and also expose construction workers to | Design, fabrication, and erection of steel shall meet the requirements noted in "OSHA STEEL ERECTION STANDARD (SUBPART R)". | Alan Speegle (Southern Co.)
543 | Miscellaneous Steel, Railing and Grating | Civil | Structural Steel Framing | Design | Safety | Structural steel erection operations can lead to collapse if adequate support is not provided for the members before permanent connection. Welding operations can create fire hazards due to excessive slag or sparks, and also expose construction workers to | Discuss with construction service representatives any OSHA 1926 Subpart R requirements that needs to be included in our steel technical specifications. | Alan Speegle (Southern Co.)
544 | Miscellaneous Steel, Railing and Grating | Civil | Structural Steel Framing | Design | Safety | Structural steel erection operations can lead to collapse if adequate support is not provided for the members before permanent connection. Welding operations can create fire hazards due to excessive slag or sparks, and also expose construction workers to | Permanent stairs with handrail, railing, stringers, grating, and treads must be designed, purchased, and installled to coinicde wiht the building steel. | Alan Speegle (Southern Co.)
545 | Miscellaneous Steel, Railing and Grating | Civil | Structural Steel Framing | Design | Safety | Structural steel erection operations can lead to collapse if adequate support is not provided for the members before permanent connection. Welding operations can create fire hazards due to excessive slag or sparks, and also expose construction workers to | Railing must be designed, purchased , and installed to coincide with the installation of the building steel. Temporary safety railing cable will be installed in those areas which will have siding or equipment. | Alan Speegle (Southern Co.)
546 | Miscellaneous Steel, Railing and Grating | Civil | Structural Steel Framing | Design | Safety | Structural steel erection operations can lead to collapse if adequate support is not provided for the members before permanent connection. Welding operations can create fire hazards due to excessive slag or sparks, and also expose construction workers to | Sumps will have steel ladder rungs for access. Steel grating and support steel will be furnished as required to support the pumps and grating. Sumps will be elevated 18-24 inches to keep vehicles off the top of the sump | Alan Speegle (Southern Co.)
547 | Miscellaneous Steel, Railing and Grating | Civil | Structural Steel Framing | Design | Safety | Structural steel erection operations can lead to collapse if adequate support is not provided for the members before permanent connection. Welding operations can create fire hazards due to excessive slag or sparks, and also expose construction workers to | Grating with pre-cut openings should have temporary plywood covers ties over them, using proper gage wire, until the openings can be secured with handrails, hatches, etc. Install the plywood covers in the shop or on the ground at the plant construction s | Alan Speegle (Southern Co.)
548 | Roof and Floor Decking | Civil | Structural Steel Framing | Design | Safety | Iron workers placing decking can expose themselves to a fall hazard. | Consider adding 1926 Subpart R Appendix D (1926.760) to the code requirements listed in the steel erection inquiry. Appendix D - Illustration of the Use of Control Lines to Demarcate Controlled Decking Zones (CDZ). | Alan Speegle (Southern Co.)
549 | Roof and Floor Decking | Civil | Structural Steel Framing | Design | Safety | Iron workers placing decking can expose themselves to a fall hazard. | CDZ Requirement: The controlled decking zone (CDZ) is defined by a control line or by any other means that restricts access | Alan Speegle (Southern Co.)
550 | Roof and Floor Decking | Civil | Structural Steel Framing | Design | Safety | Iron workers placing decking can expose themselves to a fall hazard. | CDZ Requirement: A control line for a CDZ is erected not less that 6 feet (1.8 m) nor more than 90 feet (27.4 m) from the leading edge. | Alan Speegle (Southern Co.)
551 | Roof and Floor Decking | Civil | Structural Steel Framing | Design | Safety | Iron workers placing decking can expose themselves to a fall hazard. | CDZ Requirement: Control Lines extend along the entire length of the unprotected or leading edge and are approximately parallel to the unprotected or leading edge. | Alan Speegle (Southern Co.)
552 | Roof and Floor Decking | Civil | Structural Steel Framing | Design | Safety | Iron workers placing decking can expose themselves to a fall hazard. | CDZ Requirement: Control lines are connecteed on each side to a guardrail system, wall, stanchion or other suitable anchorage. | Alan Speegle (Southern Co.)
553 | Roof and Floor Decking | Civil | Structural Steel Framing | Design | Safety | Iron workers placing decking can expose themselves to a fall hazard. | CDZ Requirement: Control lines consist of ropes, wires, tapes, or equivalent materials, and supporting stanchions. | Alan Speegle (Southern Co.)
554 | Roof and Floor Decking | Civil | Structural Steel Framing | Design | Safety | Iron workers placing decking can expose themselves to a fall hazard. | CDZ Requirement: Each line is rigged and supported in such a way that its lowest point (including sag) is not less than 39 inches (1.0 m) from the walking/working surface and its highest point is not more than 45 inches (1.3 m) from the walking/working su | Alan Speegle (Southern Co.)
555 | Roof and Floor Decking | Civil | Structural Steel Framing | Design | Safety | Iron workers placing decking can expose themselves to a fall hazard. | CDZ Requirement: Each line has a minimum breaking strength of 200 pounds (90.8 kg) | Alan Speegle (Southern Co.)
556 | Roof and Floor Decking | Civil | Structural Steel Framing | Design | Safety | Iron workers placing decking can expose themselves to a fall hazard. | Ball mill roof decking requirements will meet requirements noted in OSHA Steel Erection Standard (Subpart R). Workers will be able to tie support life lines. Some roof steel is designed for fall protection anchor loads. | Alan Speegle (Southern Co.)
557 | Platforms/Walkways | Civil | Structural Steel Framing | Design | Safety | Structural Steel Framing: Platforms/Walkways | Provide a non-slip walking surface on walkways and platforms exposed to the weather. | Alan Speegle (Southern Co.)
558 | Platforms/Walkways | Civil | Structural Steel Framing | Design | Safety | Structural Steel Framing: Platforms/Walkways | Provide multiple means of access to elevated walkways and platforms which can be used during emergency situations. | Alan Speegle (Southern Co.)
559 | Platforms/Walkways | Civil | Structural Steel Framing | Design | Safety | Structural Steel Framing: Platforms/Walkways | Use serrated grating, instead of checkered steel plate, for walking surfaces to prevent slipping hazards. | Alan Speegle (Southern Co.)
560 | Platforms/Walkways | Civil | Structural Steel Framing | Design | Safety | Structural Steel Framing: Platforms/Walkways | Design access platform large enough to install a 4'x4' scaffolding so that the expansion joints can be installed and replaced | Alan Speegle (Southern Co.)
561 | Platforms/Walkways | Civil | Structural Steel Framing | Design | Safety | Structural Steel Framing: Platforms/Walkways | We are pllanning to use steel beams, grating, and railing to access the slurry talkn agitator. Agitator platform will be 4' wide. | Alan Speegle (Southern Co.)
562 | Platforms/Walkways | Civil | Structural Steel Framing | Design | Safety | Structural Steel Framing: Platforms/Walkways | Stair riser will be 7" maximum. Stair treads will be 11" minimum. | Alan Speegle (Southern Co.)
563 | Ductwork: Demolition and Modification of Existing | Civil | Structural Steel Framing | Design | Safety | Never assume the erector will use sound judgement when domolishing existing ductwork. | Provide design documents for location of temporary bracing and a written procedure for the order of installation of modification material to preserve the correct geometry and structural integrity of the existing ductwork during demolition and modification | Alan Speegle (Southern Co.)
564 | Ductwork: Demolition and Modification of Existing | Civil | Structural Steel Framing | Design | Safety | Never assume the erector will use sound judgement when domolishing existing ductwork. | When connection new stiffener framing to existing stiffener framing, design the connection to provide maximum flexibility in fit-up and welding for ease of installation. | Alan Speegle (Southern Co.)
565 | Ductwork: Demolition and Modification of Existing | Civil | Structural Steel Framing | Design | Safety | Never assume the erector will use sound judgement when domolishing existing ductwork. | When a portion of the existing duct will be preserved and a new piece of ductwork will tie-in, the tie-in point should be an easily reinforced point, preferably at an existing stiffener, binder or truss. | Alan Speegle (Southern Co.)
566 | Ductwork: Demolition and Modification of Existing | Civil | Structural Steel Framing | Design | Safety | Never assume the erector will use sound judgement when domolishing existing ductwork. | Engineering will provide a drawing showing hte duct cut line and a duct removal and damper installation sequence. | Alan Speegle (Southern Co.)
567 | Ductwork: Preservation and Strengthening of Existing | Civil | Structural Steel Framing | Design | Safety | Existing ductwork will normally be in poor condition. | Provide a procedure to thoroughly inspect the ductwork both inside and outside, paying close attention to skin plate thickness, external stiffener web and flange thickness, external stiffener connections, internal pipe bracing wall thickness and internal | Alan Speegle (Southern Co.)
568 | Ductwork: Preservation and Strengthening of Existing | Civil | Structural Steel Framing | Design | Safety | Existing ductwork will normally be in poor condition. | Provide details for removal/replacement of internal pipe bracing and modification/strengthening of pipe bracing connections. | Alan Speegle (Southern Co.)
569 | Ductwork: Preservation and Strengthening of Existing | Civil | Structural Steel Framing | Design | Safety | Existing ductwork will normally be in poor condition. | Provide details for replacing/patching thin portions of the ductwork skin plate. | Alan Speegle (Southern Co.)
570 | Ductwork: Preservation and Strengthening of Existing | Civil | Structural Steel Framing | Design | Safety | Existing ductwork will normally be in poor condition. | Provide details for modification /strengthening external stiffener connections. | Alan Speegle (Southern Co.)
571 | Ductwork: Preservation and Strengthening of Existing | Civil | Structural Steel Framing | Design | Safety | Existing ductwork will normally be in poor condition. | Provide details for adding new or strengthening external stiffeners. | Alan Speegle (Southern Co.)
572 | Ductwork: Preservation and Strengthening of Existing | Civil | Structural Steel Framing | Design | Safety | Existing ductwork will normally be in poor condition. | Provide a detailed procedure for systematic removal/replacement of modification/strengthening. | Alan Speegle (Southern Co.)
573 | Ductwork: Preservation and Strengthening of Existing | Civil | Structural Steel Framing | Design | Safety | Existing ductwork will normally be in poor condition. | Consider the economy of duct replacement vs preservation and strengthening. | Alan Speegle (Southern Co.)
574 | Ductwork: Construction Friendly Design | Civil | Structural Steel Framing | Design | Safety | Remember to keep it simple. | Utilize field bolts rather that field welding where possible since bolted connections can be correctly made by less highly trained personnel than welded connections. | Alan Speegle (Southern Co.)
575 | Ductwork: Construction Friendly Design | Civil | Structural Steel Framing | Design | Safety | Remember to keep it simple. | Avoid hard mating surfaces since they require very close tolerance. | Alan Speegle (Southern Co.)
576 | Ductwork: Construction Friendly Design | Civil | Structural Steel Framing | Design | Safety | Remember to keep it simple. | Where hard mating surfaces are required, consider using variable thickness shim packs to facilitate erection. | Alan Speegle (Southern Co.)
577 | Ductwork: Construction Friendly Design | Civil | Structural Steel Framing | Design | Safety | Remember to keep it simple. | Where field connections are required, connections should be designed to allow use of temporary pins or support of the members until welding is complete. | Alan Speegle (Southern Co.)
578 | Ductwork: Construction Friendly Design | Civil | Structural Steel Framing | Design | Safety | Remember to keep it simple. | All field connections should allow for reasonable access of construction personnel. | Alan Speegle (Southern Co.)
579 | Ductwork: Construction Friendly Design | Civil | Structural Steel Framing | Design | Safety | Remember to keep it simple. | Flue gas ductwork will have continuous walkways along one side of horizontal duct runs. Man doors will be spaced at 200 feet on center. Several stair towers will provide access to the walkway outside the duct. | Alan Speegle (Southern Co.)
580 | Ductwork: Construction Friendly Design | Civil | Structural Steel Framing | Design | Safety | Remember to keep it simple. | Flue gas steel duct fabricator shall test shop welds for leaks. This will be noted in the specifications or on the drawings. The flue gas duct erector shall test field welds for leaks. | Alan Speegle (Southern Co.)
581 | Ductwork: Construction Friendly Design | Civil | Structural Steel Framing | Design | Safety | Remember to keep it simple. | The flue gas duct work and/or duct support steel will be designed for construction loads associated with the installation of walk boards and support brackets for construction workers. | Alan Speegle (Southern Co.)
582 | Ductwork: Construction Friendly Design | Civil | Structural Steel Framing | Design | Safety | Remember to keep it simple. | Flue gas duct work insulation may be installed on the ground except items note in 3. We assume 1) The C-shaped duct fabricated pieces will be joined in the field on the ground, 2) 20-foot sections of duct will be joined on the ground or in the air, and 3 | Alan Speegle (Southern Co.)
583 | Ductwork: Construction Friendly Design | Civil | Structural Steel Framing | Design | Safety | Remember to keep it simple. | Trucking the 2 modules either bolted or welded and nested together on the truck | Alan Speegle (Southern Co.)
584 | Ductwork: Construction Friendly Design | Civil | Structural Steel Framing | Design | Safety | Remember to keep it simple. | Specify tolerances on the duct sections | Alan Speegle (Southern Co.)
585 | Ductwork: Construction Friendly Design | Civil | Structural Steel Framing | Design | Safety | Remember to keep it simple. | Specify back to back flanges with the field sealing them together with a continuous butt weld. | Alan Speegle (Southern Co.)
586 | Ductwork: Construction Friendly Design | Civil | Structural Steel Framing | Design | Safety | Remember to keep it simple. | Stagger the bolts in the back to back channels to better pull each of the channel flanges together. | Alan Speegle (Southern Co.)
587 | Ductwork: Construction Friendly Design | Civil | Structural Steel Framing | Design | Safety | Remember to keep it simple. | Specify MC channel shapes at the support frames. | Alan Speegle (Southern Co.)
588 | Ductwork: Construction Friendly Design | Civil | Structural Steel Framing | Design | Safety | Remember to keep it simple. | Large quantities will need to place an order from the mill as early as possible. | Alan Speegle (Southern Co.)
589 | Ductwork: Construction Friendly Design | Civil | Structural Steel Framing | Design | Safety | Remember to keep it simple. | Large quantities need to place an order from the mill as early as possible. | Alan Speegle (Southern Co.)
590 | Ductwork: Construction Friendly Design | Civil | Structural Steel Framing | Design | Safety | Remember to keep it simple. | Some fabrications need to hire a third party vendor to provide any site assembly of panels. | Alan Speegle (Southern Co.)
591 | Ductwork: Construction Friendly Design | Civil | Structural Steel Framing | Design | Safety | Remember to keep it simple. | Consider large oversize "C" sections at plants such as Wansley. These loads would be over 15'-0" wide and use two escorts. The cost of these shipments versus field assembly needs to be studied. | Alan Speegle (Southern Co.)
592 | Ductwork: Construction Friendly Design | Civil | Structural Steel Framing | Design | Safety | Remember to keep it simple. | Consider purchase of 6'-0" wide plate and splice at intermediate stiffeners. | Alan Speegle (Southern Co.)
593 | Ductwork: Construction Friendly Design | Civil | Structural Steel Framing | Design | Safety | Remember to keep it simple. | Consider bolting cross members across both "C" sections for shipping and handling. | Alan Speegle (Southern Co.)
594 | Ductwork: Construction Friendly Design | Civil | Structural Steel Framing | Design | Safety | Remember to keep it simple. | Civil ductwork drawings should show the design pressure. This will make is easier for plant and engineeriing personnel to determine this design paramated in the future. | Alan Speegle (Southern Co.)
595 | Ductwork: Construction Friendly Design | Civil | Structural Steel Framing | Design | Safety | Remember to keep it simple. | When barge access is available, consider shop assemble of larger duct modules. | Alan Speegle (Southern Co.)
596 | Hazardous Conditions | Mechanical | Tank, Vessel | Design | Safety | Tanks can present confined space, toxic substance, fire, and explosion hazards for construction workers. | Avoid interior welds in tanks. Provide ventilation in the tank if interior welds are required. | Alan Speegle (Southern Co.)
597 | Hazardous Conditions | Mechanical | Tank, Vessel | Design | Safety | Tanks can present confined space, toxic substance, fire, and explosion hazards for construction workers. | Provide vents and overflow or relief devices to avoid over-pressurization, and to avoid creating sufficient vacuum to cause the tank to collapse. | Alan Speegle (Southern Co.)
598 | Hazardous Conditions | Mechanical | Tank, Vessel | Design | Safety | Tanks can present confined space, toxic substance, fire, and explosion hazards for construction workers. | Provide dikes around storage tanks which contain hazardous substances. Use a slab rather than an HDPE liner for the leak detection (LD) system on the bottom of large storage tanks. | Alan Speegle (Southern Co.)
599 | Hazardous Conditions | Mechanical | Tank, Vessel | Design | Safety | Tanks can present confined space, toxic substance, fire, and explosion hazards for construction workers. | Provide traps or valves on process sewers and area drains to avoid the spread of fire in case of a ruptured tank. | Alan Speegle (Southern Co.)
600 | Hazardous Conditions | Mechanical | Tank, Vessel | Design | Safety | Tanks can present confined space, toxic substance, fire, and explosion hazards for construction workers. | Ensure that tanks and vessels meet all local, state, and federal design code requirements. | Alan Speegle (Southern Co.)
601 | Tank Erection | Civil; Mechanical | Tank, Vessel | Design | Safety | The erection and/or placement process used for tanks and vessels can lead to safety hazards for construction workers. | Fabricate tank roofs at grade and lift them into place as one assembly. | Alan Speegle (Southern Co.)
602 | Tank Erection | Civil; Mechanical | Tank, Vessel | Design | Safety | The erection and/or placement process used for tanks and vessels can lead to safety hazards for construction workers. | Complete interior welds on tank walls before erecting the roof. | Alan Speegle (Southern Co.)
603 | Tank Erection | Civil; Mechanical | Tank, Vessel | Design | Safety | The erection and/or placement process used for tanks and vessels can lead to safety hazards for construction workers. | Provide a guardrail along the perimeter of the tank roof. | Alan Speegle (Southern Co.)
604 | Tank Erection | Civil; Mechanical | Tank, Vessel | Design | Safety | The erection and/or placement process used for tanks and vessels can lead to safety hazards for construction workers. | Provide connection points for lifelines at the center of the tank roof. | Alan Speegle (Southern Co.)
605 | Underground Tanks | Civil; Mechanical | Tank, Vessel | Design | Safety | Underground tanks and vessels which are not adequately protected can be safety hazards for construction workers. | Protect underground tanks and vessels against crushing by use of sleeves, concrete slabs, or by providing guard posts to prevent travel over them. | Alan Speegle (Southern Co.)
606 | Tank Entrances | Mechanical | Tank, Vessel | Design | Safety | Without adequate entrances and ventilation, tanks and vessels can create confined space hazards. | Locate permanent atmosphere testing devices and forced air ventilation equipment at entrances to tanks and vessels. | Alan Speegle (Southern Co.)
607 | Tank Entrances | Mechanical | Tank, Vessel | Design | Safety | Without adequate entrances and ventilation, tanks and vessels can create confined space hazards. | Provide connection points adjacent tank and vessel entrances for attachment of a lifeline or safety harness. | Alan Speegle (Southern Co.)
608 | Tank Entrances | Mechanical | Tank, Vessel | Design | Safety | Without adequate entrances and ventilation, tanks and vessels can create confined space hazards. | Provide at least two access ports for tanks and vessels to aid in access/egress and ventilation. | Alan Speegle (Southern Co.)
609 | Tank Entrances | Mechanical | Tank, Vessel | Design | Safety | Without adequate entrances and ventilation, tanks and vessels can create confined space hazards. | Provide for a door to be installed in floating roofs for large vessels. Design and schedule the door to be installed prior to erection of the roof. | Alan Speegle (Southern Co.)
610 | Tank Stairs | Civil; Mechanical | Tank, Vessel | Design | Safety | The design of stairs for large tanks and vessels can lead to fall hazards for construction workers. | Coordinate the layout of tank stair landings with the tank foundation design to prevent tripping hazards. | Alan Speegle (Southern Co.)
611 | Tank Stairs | Civil; Mechanical | Tank, Vessel | Design | Safety | The design of stairs for large tanks and vessels can lead to fall hazards for construction workers. | Design circumferential stairs around tanks to ascend clockwise. | Alan Speegle (Southern Co.)
612 | Designs | Civil | Constructability | Design | Safety | Without adequate knowledge of the project design concept, complicated or unique designs can lead to construction site hazards. | Engineering should provide, or require the constructor to submit, directions for a construction sequence in complicated or unique designs. | Alan Speegle (Southern Co.)
613 | Designs | Civil | Constructability | Design | Safety | Without adequate knowledge of the project design concept, complicated or unique designs can lead to construction site hazards. | Conduct constructability reviews early in the design phase. Include the constructor and maintenance personnel in the reviews. | Alan Speegle (Southern Co.)
614 | Fire Hazards | Civil; Mechanical | Constructability | Design | Safety | The scheduled construction or demolition of fire prevention devices can lead to fire hazards for construction workers. | Provide engineering documents and schedule an underground firewater system to be constructed at the beginning of the project. | Alan Speegle (Southern Co.)
615 | Fire Hazards | Civil; Mechanical | Constructability | Design | Safety | The scheduled construction or demolition of fire prevention devices can lead to fire hazards for construction workers. | Engineering should show requirements for permanent emergency exit and egress signs to be erected early in construction. | Alan Speegle (Southern Co.)
616 | Fire Hazards | Civil; Mechanical | Constructability | Design | Safety | The scheduled construction or demolition of fire prevention devices can lead to fire hazards for construction workers. | Release engineering documents timely so that fire walls and fire doors may be constructed or placed early in the construction phase. | Alan Speegle (Southern Co.)
617 | Roadways | Civil | Constructability | Design | Safety | The work schedule and construction sequence for plant road construction and maintenance can affect the safety of construction workers. | Prior to the start of the project, erect informational signs near the project site announcing the construction work and schedule. | Alan Speegle (Southern Co.)
618 | Roadways | Civil | Constructability | Design | Safety | The work schedule and construction sequence for plant road construction and maintenance can affect the safety of construction workers. | Discuss road drawing release dated with construction services representatives. Consider providing good access for the prime contractor, especially in wet weather. | Alan Speegle (Southern Co.)
619 | Stairways | Civil | Constructability | Design | Safety | Timely erection of permanent stairways and handrails can help eliminate falls and other hazards associated with temporary stairs and scaffolding. | Provide engineering documents and schedule permanent stairways to be constructed as soon as possible. | Alan Speegle (Southern Co.)
620 | Stairways | Civil | Constructability | Design | Safety | Timely erection of permanent stairways and handrails can help eliminate falls and other hazards associated with temporary stairs and scaffolding. | Provide engineering documents and schedule permanent railings to be shipped and erected along with the structural steel as one assembly. | Alan Speegle (Southern Co.)
621 | Workers | Civil | Constructability | Design | Safety | Construction schedules can affect worker safety and health if the schedules do not allow for sufficient safety planning and recognize worker health requirements. | Schedule the release of engineering drawings such that sufficient time is allowed for materials to be purchased, delivered, and installed. | Alan Speegle (Southern Co.)
622 | Electrical | Electrical | Constructability | Design | Safety | The scheduled construction of electrical lines and equipment can lead to safety hazards for construction workers. | Provide engineering documents to support permanent telephone lines to be installed early in the construction phase. Locate the lines in remote buildings, process areas, and on the site perimeter. | Alan Speegle (Southern Co.)
623 | Electrical | Electrical | Constructability | Design | Safety | The scheduled construction of electrical lines and equipment can lead to safety hazards for construction workers. | Provide the engineering documents to support the installation of the permanent electrical system. | Alan Speegle (Southern Co.)
624 | Electrical | Electrical | Constructability | Design | Safety | The scheduled construction of electrical lines and equipment can lead to safety hazards for construction workers. | Provide engineering documents to support the early installation of permanent lighting systems. | Alan Speegle (Southern Co.)
625 | Electrical | Electrical | Constructability | Design | Safety | The scheduled construction of electrical lines and equipment can lead to safety hazards for construction workers. | If existing electrical lines need to be in service during construction, consider the possibility of reducing the voltage or current before construction begins. | Alan Speegle (Southern Co.)
626 | Elevated Work | Civil | Constructability | Design | Safety | The work schedule and construction sequence for work performed at elevated levels can affect the safety of construction workers. | Provide engineering documents that are user-friendly to pre-fabricate building components in the shop or pre-assembled pieces on the ground and erect them as one assembly. | Alan Speegle (Southern Co.)
627 | Elevated Work | Civil | Constructability | Design | Safety | The work schedule and construction sequence for work performed at elevated levels can affect the safety of construction workers. | Provide engineering documents to allow exterior wall structure and/or finish to go up with the framework or soon thereafter. | Alan Speegle (Southern Co.)
628 | Existing Structure | Civil | Constructability | Design | Safety | The work schedule and sequence for projects which require work with an existing structure or utilities can lead to safety hazards for construction workers. | Engineer should provide a construction sequence of removing and add structural steel and/or concrete framing for structures with major rework. | Alan Speegle (Southern Co.)
629 | Existing Structure | Civil | Constructability | Design | Safety | The work schedule and sequence for projects which require work with an existing structure or utilities can lead to safety hazards for construction workers. | Engineering documents should provide a work sequence for safe tie-ins to existing utilities. | Alan Speegle (Southern Co.)
630 | Mechanical/HVAC | Mechanical | Constructability | Design | Safety | The scheduled construction of mechanical and HVAC equipment can lead to safety hazards for construction workers. | Schedule air conditioning, heating, and ventilating systems to be available for use by the constructor at close-in. | Alan Speegle (Southern Co.)
631 | Mechanical/HVAC | Mechanical | Constructability | Design | Safety | The scheduled construction of mechanical and HVAC equipment can lead to safety hazards for construction workers. | Design and schedule ventilating systems to be in place in areas where coatings will be applied prior to applying the coatings. | Alan Speegle (Southern Co.)
632 | Mechanical/HVAC | Civil | Constructability | Design | Safety | The scheduled construction of mechanical and HVAC equipment can lead to safety hazards for construction workers. | Engineering specifications should require shop painting of materials, piping, and equipment. | Alan Speegle (Southern Co.)
633 | Testing | Civil | Constructability | Design | Safety | Timely testing of new construction materials and work in place can eliminate safety hazards for construction workers. | Specify concrete test results to be verified before removal of the forms and shoring. | Alan Speegle (Southern Co.)
634 | Testing | Civil | Constructability | Design | Safety | Timely testing of new construction materials and work in place can eliminate safety hazards for construction workers. | Concrete specifications should reference ACI code requirements for removing concrete forms and shores. | Alan Speegle (Southern Co.)
635 | Existing Structure | Civil | Existing Buildings | Design | Safety | Working with an existing structure can lead to collapse hazards if the constructor lacks knowledge of the existing structure's loading conditions and structural integrity. | Review code requirements to determine if your modification requires you to bring the structure up to current code. | Alan Speegle (Southern Co.)
636 | Existing Structure | Civil | Existing Buildings | Design | Safety | Working with an existing structure can lead to collapse hazards if the constructor lacks knowledge of the existing structure's loading conditions and structural integrity. | Indicate on the contract drawings the locations where shoring of the existing structure is required during construction. | Alan Speegle (Southern Co.)
637 | Existing Structure | Civil | Existing Buildings | Design | Safety | Working with an existing structure can lead to collapse hazards if the constructor lacks knowledge of the existing structure's loading conditions and structural integrity. | Review the condition and integrity of the existing structure and indicate any known hazards or deficiencies on the contract drawings. | Alan Speegle (Southern Co.)
638 | Existing Structure | Civil | Existing Buildings | Design | Safety | Working with an existing structure can lead to collapse hazards if the constructor lacks knowledge of the existing structure's loading conditions and structural integrity. | When working on or near existing structures, consider using bolted, rather than welded, connections to minimize the fire hazard. | Alan Speegle (Southern Co.)
639 | Existing Structure | Civil | Existing Buildings | Design | Safety | Working with an existing structure can lead to collapse hazards if the constructor lacks knowledge of the existing structure's loading conditions and structural integrity. | Engineering should consider requiring the constructor to locate and mark the existing reinforcing steel prior to cutting into existing reinforced concrete members. | Alan Speegle (Southern Co.)
640 | Existing Structure | Civil | Existing Buildings | Design | Safety | Working with an existing structure can lead to collapse hazards if the constructor lacks knowledge of the existing structure's loading conditions and structural integrity. | Specify modification sequence if the reworks inpacts the stability of the structure. | Alan Speegle (Southern Co.)
641 | Utilities | Civil | Existing Buildings | Design | Safety | A lack of access to or knowledge of existing utilities can affect the safety of construction workers in emergency situations and during excavation operations. | Indicate on the contract drawings the locations of shut-off valves and switches for existing utilities. Provide the constructor with access to these locations. | Alan Speegle (Southern Co.)
642 | Utilities | Civil | Existing Buildings | Design | Safety | A lack of access to or knowledge of existing utilities can affect the safety of construction workers in emergency situations and during excavation operations. | Indicate on the contract drawings the locations of existing underground utilities and mark a clear zone around the utilities. | Alan Speegle (Southern Co.)
643 | Utilities | Civil | Existing Buildings | Design | Safety | A lack of access to or knowledge of existing utilities can affect the safety of construction workers in emergency situations and during excavation operations. | Include the name, address, and telephone number of local utility companies on the drawings. | Alan Speegle (Southern Co.)
644 | Utilities | Civil | Existing Buildings | Design | Safety | A lack of access to or knowledge of existing utilities can affect the safety of construction workers in emergency situations and during excavation operations. | Note on the drawings the source of information and level of certainty on the location of underground utilities. | Alan Speegle (Southern Co.)
645 | Fire Hazards | Civil | Existing Buildings | Design | Safety | Structures which contain or are constructed of combustible materials can be fire hazards during the construction phase. | Limit the spread of fire by designing fire walls, parapets, fire stops, deluge systems, etc. | Alan Speegle (Southern Co.)
646 | Demolition | Civil | Existing Buildings | Design | Safety | Plan what the demolition documents will look like and who will be responsible for the documents. | The plant personnel and project team must all understand the scope of work for demolition. | Alan Speegle (Southern Co.)
647 | Demolition | Civil | Existing Buildings | Design | Safety | Plan what the demolition documents will look like and who will be responsible for the documents. | Plan who will provide the demolition drawings. | Alan Speegle (Southern Co.)
648 | Demolition | Civil | Existing Buildings | Design | Safety | Plan what the demolition documents will look like and who will be responsible for the documents. | Plan how demolition drawings and pictures can effectively show the required demoliton. Determine if a sequence of demolition is required to maintain a safe structure. | Alan Speegle (Southern Co.)
649 | Demolition | Civil | Existing Buildings | Design | Safety | Plan what the demolition documents will look like and who will be responsible for the documents. | Engineering and Construction Services personnel show discuss and agree on the engineering and construction schedule. | Alan Speegle (Southern Co.)
650 | Demolition | Civil | Existing Buildings | Design | Safety | Plan what the demolition documents will look like and who will be responsible for the documents. | Evaluate where removed material will be placed. | Alan Speegle (Southern Co.)
651 | Demolition | Civil | Existing Buildings | Design | Safety | Plan what the demolition documents will look like and who will be responsible for the documents. | Determine if any hazardous materials, such as asbetos, are present. | Alan Speegle (Southern Co.)
652 | Demolition | Civil | Existing Buildings | Design | Safety | Plan what the demolition documents will look like and who will be responsible for the documents. | Evaluate if there is any salvageable material. | Alan Speegle (Southern Co.)
653 | Demolition | Civil | Existing Buildings | Design | Safety | Plan what the demolition documents will look like and who will be responsible for the documents. | Determine the impact of utilities and services in the area of demolition. | Alan Speegle (Southern Co.)
654 | Area Classification | I&C | I&C | Design | Safety | Ensure instrument/devices located in hazardous areas meet design requirements for that area. | Ensure instrument/devices requiring special design (purging, etc) have been reviewed, evaluated and are in compliance with project codes and standards. | Alan Speegle (Southern Co.)
655 | Area Classification | I&C | I&C | Design | Safety | Ensure instrument/devices located in hazardous areas meet design requirements for that area. | Ensure instrument/devices are identified, classified, and shown on the project drawings. | Alan Speegle (Southern Co.)
656 | Area Classification | I&C | I&C | Design | Safety | Ensure instrument/devices located in hazardous areas meet design requirements for that area. | Ensure warning labels and signs are provided to address warning and hazardous information to prevent possible property damage or personal injury. | Alan Speegle (Southern Co.)
657 | Area Classification | I&C | I&C | Design | Safety | Ensure instrument/devices located in hazardous areas meet design requirements for that area. | Ensure warning labels and signs comply with codes and standards and are properly positioned. | Alan Speegle (Southern Co.)
658 | Design | I&C | I&C | Design | Safety | Codes, Standards, Requirements and Performance | Ensure design is in compliance with project codes and standards. Ensure instrument design is in compliance with Quality Standard for Instrument Air ANSI/ISA-S7.0.01-2004 (IEC 61511-1 Mod). Ensure design for boiler drum level indicators are in compliance | Alan Speegle (Southern Co.)
659 | Design | I&C | I&C | Design | Safety | Codes, Standards, Requirements and Performance | Ensure instrument performance and accuracy shall fulfill process and unit performance requirements for the project. | Alan Speegle (Southern Co.)
660 | Design | I&C | I&C | Design | Safety | Codes, Standards, Requirements and Performance | Ensure that variations in instrument and control types, material, ranges, etc. are kept to a minimum. Tubing size and material should be kept to a standard to minimize confusion in identifying. | Alan Speegle (Southern Co.)
661 | Design | I&C | I&C | Design | Safety | Codes, Standards, Requirements and Performance | Ensure temperature elements are designed ungrounded. Temperature elements are preferably not be grounded at the point of measurement. | Alan Speegle (Southern Co.)
662 | Design | I&C | I&C | Design | Safety | Codes, Standards, Requirements and Performance | Ensure thermowells are provided with all thermo elements and are in compliance with project codes and standards. Ensure thermocouple terminals are bakelite construction. | Alan Speegle (Southern Co.)
663 | Design | I&C | I&C | Design | Safety | Codes, Standards, Requirements and Performance | Ensure thermowells are within the range of ASME PTC 19.3. Ensure thermowells are designed to prevent damage caused by vortex-induced vibration over the range of velocities to be encountered. Ensure thermowells are designed with nipple-union-nipple exten | Alan Speegle (Southern Co.)
664 | Design | I&C | I&C | Design | Safety | Codes, Standards, Requirements and Performance | Ensure instruments/devices are compatible with process parameters associated with the project. Ensure design of transmitters are within their calibration range. Eliminate special equipment calibration, if possible. No transmitter will be selected for u | Alan Speegle (Southern Co.)
665 | Design | I&C | I&C | Design | Safety | Codes, Standards, Requirements and Performance | Ensure instruments/devices are design for environmental conditions associated with the project. Level gauge glasses and site flow indicators shall not be used for ammonia services. | Alan Speegle (Southern Co.)
666 | Design | I&C | I&C | Design | Safety | Codes, Standards, Requirements and Performance | Ensure other design disciplines are informed concerning equipment loading. Equipment heat load for control building HVAC systems. Equipment electrical load for instrumentation and control systems. Equipment weight load for piping or structural supports | Alan Speegle (Southern Co.)
667 | Design | I&C | I&C | Design | Safety | Codes, Standards, Requirements and Performance | Ensure station service support is adequate and indicated on the project schedule. Determine control system requirements and schedule. Determine building is adequate for control systems. Determine power available. Determine HVAC available. Determine s | Alan Speegle (Southern Co.)
668 | Design | I&C | I&C | Design | Safety | Codes, Standards, Requirements and Performance | Ensure construction storage is adequate for instrumentation, control systems, etc. Determine storage will protect equipment from the weather and abuse. | Alan Speegle (Southern Co.)
669 | Design | I&C | I&C | Design | Safety | Codes, Standards, Requirements and Performance | Communicate constructability review needs early in the project to project management. | Alan Speegle (Southern Co.)
670 | Design | I&C | I&C | Design | Safety | Codes, Standards, Requirements and Performance | Ensure controls system communications are checked for compatibility. | Alan Speegle (Southern Co.)
671 | Design | I&C | I&C | Design | Safety | Codes, Standards, Requirements and Performance | Ensure design for accessibility for instrumentation and accessories is complete. Root valves within easy reach. Drain and blow-down valves within easy reach. | Alan Speegle (Southern Co.)
672 | Design | I&C | I&C | Design | Safety | Codes, Standards, Requirements and Performance | Design to minimize device locations within confined spaces. | Alan Speegle (Southern Co.)
673 | Design | I&C | I&C | Design | Safety | Codes, Standards, Requirements and Performance | Design connections to be assembled in the shop rather than the field if possible. Assist to assemble flow elements in piping before lifting to pipe racks. | Alan Speegle (Southern Co.)
674 | Design | I&C | I&C | Design | Safety | Codes, Standards, Requirements and Performance | Design instruments/devices for purging cycles or interlocked for hazardous areas. | Alan Speegle (Southern Co.)
675 | Design | I&C | I&C | Design | Safety | Codes, Standards, Requirements and Performance | Ensure design for disabilities requirements associated with the project are communicated and documented. | Alan Speegle (Southern Co.)
676 | Design | I&C | I&C | Design | Safety | Codes, Standards, Requirements and Performance | Ensure design redundancy is engineered to increase reliability and reduce failures. Determine redundancy in design to reduce equipment failures. Determine the common cause and common mode of failure. Dedicated process switches will not be used when red | Alan Speegle (Southern Co.)
677 | Design | I&C | I&C | Design | Safety | Codes, Standards, Requirements and Performance | Ensure a clear understanding of the plants process safety design requirements is communicated to design personnel. Ensure that the client understands the limitation of the project design and is fully aware of these limitations. | Alan Speegle (Southern Co.)
678 | Compatibility | I&C | I&C | Design | Safety | Process and Codes & Standards Compatible | Ensure instrument/devices are designed to be compatible with fluid and are in compliance with codes and standards. Ensure instrument/device material (gaskets, diaphragms, o-rings, etc) that comes in contact with hazardous, corrosive or contaminated fluid | Alan Speegle (Southern Co.)
679 | Compatibility | I&C | I&C | Design | Safety | Process and Codes & Standards Compatible | Ensure the existing equipment and control systems are compatible with the project design codes and standards. | Alan Speegle (Southern Co.)
680 | Construction | I&C | I&C | Design | Safety | Deliverables, Procurement and Support Schedules | Ensure drawing delivery schedules are reviewed to provide documentation to construction in a timely manner. Ensure construction sequences have been reviewed to support document receipt. | Alan Speegle (Southern Co.)
681 | Construction | I&C | I&C | Design | Safety | Deliverables, Procurement and Support Schedules | Ensure procurement schedule have been reviewed to support equipment delivery. Ensure construction sequence have been reviewed to provide adequate storage of instrument and control equipment delivery. | Alan Speegle (Southern Co.)
682 | Construction | I&C | I&C | Design | Safety | Deliverables, Procurement and Support Schedules | Ensure construction schedule have been reviewed to support check-out, start-up and commissioning assistance by instrument & controls engineering personnel. | Alan Speegle (Southern Co.)
683 | Communication | I&C | I&C | Design | Safety | OIS and GENGuard Communication | Ensure all control systems requiring communication with Plant Operating Information System (OIS) are in compliance with standards. | Alan Speegle (Southern Co.)
684 | Communication | I&C | I&C | Design | Safety | OIS and GENGuard Communication | Ensure the Present Standards and Guidelines for GENGuard has been implemented. Objective of the GENGuard Program is to: (1) Raising awareness of risks associated with security issues. (2) Establishing and implementing Standards and Guidelines. (3) Est | Alan Speegle (Southern Co.)
685 | Controls | I&C | I&C | Design | Safety | Codes, Standards, Requirements and Performance | Ensure design is in compliance with project codes, standards, procedures, and guidelines. Ensure Fossil Fuel Power Plant Human-Machine Interface: Task Analysis ISA-RP77.60.05-2001 has been reviewed. Ensure Fossil Fuel Power Plant Human-Machine Interface | Alan Speegle (Southern Co.)
686 | Controls | I&C | I&C | Design | Safety | Codes, Standards, Requirements and Performance | Ensure controls are in compliance with Boiler and Combustion Systems Hazards Code NFPA 85. | Alan Speegle (Southern Co.)
687 | Controls | I&C | I&C | Design | Safety | Codes, Standards, Requirements and Performance | Ensure Logic is designed and reviewed in accordance with project parameters. | Alan Speegle (Southern Co.)
688 | Controls | I&C | I&C | Design | Safety | Codes, Standards, Requirements and Performance | Ensure components in system, which are paired to back up each other, will have a standby mode imposed upon the protective interlock scheme. | Alan Speegle (Southern Co.)
689 | Controls | I&C | I&C | Design | Safety | Codes, Standards, Requirements and Performance | Ensure workstations are in compliance with project codes and standards. | Alan Speegle (Southern Co.)
690 | Controls | I&C | I&C | Design | Safety | Codes, Standards, Requirements and Performance | Ensure controls software (configuration, graphics, etc.) are backed up regularly with two (2) copies (one backup on site and the other backup off site). | Alan Speegle (Southern Co.)
691 | Controls | I&C | I&C | Design | Safety | Codes, Standards, Requirements and Performance | Ensure repetitive motion activities of operators are avoided, if at all possible. | Alan Speegle (Southern Co.)
692 | Controls | I&C | I&C | Design | Safety | Codes, Standards, Requirements and Performance | Ensure controls are in compliance with “Safety Instrumented Systems and have been reviewed in accordance with ANSI/ISA-S84-00-01-2004 (IEC 61511-1 Mod). Ensure a checklist has been designed for Safety Instrumented Systems. Ensure adequate support is ava | Alan Speegle (Southern Co.)
693 | Controls | I&C | I&C | Design | Safety | Codes, Standards, Requirements and Performance | As soon as possible, ensure time and dates are included in the engineering and construction schedule for engineering field support. | Alan Speegle (Southern Co.)
694 | Controls | I&C | I&C | Design | Safety | Codes, Standards, Requirements and Performance | Ensure adequate access to controls equipment for ease of operation. | Alan Speegle (Southern Co.)
695 | Controls | I&C | I&C | Design | Safety | Codes, Standards, Requirements and Performance | Ensure purging, equipment cycles and special interlocks are reviewed and simulated. | Alan Speegle (Southern Co.)
696 | Controls | I&C | I&C | Design | Safety | Codes, Standards, Requirements and Performance | Ensure motors and associated equipment are designed for safe operation within the project parameters. Motor are prevented from being started if the starting permissives required for safe operation are not satisfied. Motors will automatically stop under | Alan Speegle (Southern Co.)
697 | Electrical | I&C | I&C | Design | Safety | Instruments & Controls Electrical Design Requirements. | Ensure cable, wire, and accessories are in accordance with the "Cable and Cable Bus Standard for Fossil/Hydro Projects" | Alan Speegle (Southern Co.)
698 | Electrical | I&C | I&C | Design | Safety | Instruments & Controls Electrical Design Requirements. | Ensure PVC insulated wiring is not in project design. | Alan Speegle (Southern Co.)
699 | Electrical | I&C | I&C | Design | Safety | Instruments & Controls Electrical Design Requirements. | Ensure tubing is not routed in the same tray as electrical wiring and cable. | Alan Speegle (Southern Co.)
700 | Electrical | I&C | I&C | Design | Safety | Instruments & Controls Electrical Design Requirements. | Ensure electrical connections on instruments/devices are from the bottom or side of the device. | Alan Speegle (Southern Co.)
701 | Electrical | I&C | I&C | Design | Safety | Instruments & Controls Electrical Design Requirements. | Ensure power and controls wiring and cables are separated and not routed within the same tray. | Alan Speegle (Southern Co.)
702 | Electrical | I&C | I&C | Design | Safety | Instruments & Controls Electrical Design Requirements. | Ensure fiber optic cables are design for reliability and safety. | Alan Speegle (Southern Co.)
703 | Electrical | I&C | I&C | Design | Safety | Instruments & Controls Electrical Design Requirements. | Ensure a disconnect means is provided for all sources of power supply to the equipment. For electrical power there must be an air gap between the line and/or equipment and all sources of power. The clearance shall be verified in that the equipment has b | Alan Speegle (Southern Co.)
704 | Elevated Work | I&C | I&C | Design | Safety | Assembly and Supports. | Design instruments & controls devices within the piping and support assembly design. | Alan Speegle (Southern Co.)
705 | Elevated Work | I&C | I&C | Design | Safety | Assembly and Supports. | Design flow meter runs and other major equipment to be assembled before lifting. | Alan Speegle (Southern Co.)
706 | Enclosures | I&C | I&C | Design | Safety | Instrument Enclosures must meet environmental conditions. | Ensure enclosures are adequate for the expected environmental and climate conditions. | Alan Speegle (Southern Co.)
707 | Enclosures | I&C | I&C | Design | Safety | Instrument Enclosures must meet environmental conditions. | Ensure enclosures are supplied with adequate heater and ventilation. | Alan Speegle (Southern Co.)
708 | Existing | I&C | I&C | Design | Safety | Interacting with existing equipment requires extra attention. | Ensure the design and schedule for safe tie-ins to existing utilities have been reviewed and documented. Ensure the design for tie-ins have been reviewed to correspond with the construction schedule. Ensure adequate resources are available for the tie-i | Alan Speegle (Southern Co.)
709 | Existing | I&C | I&C | Design | Safety | Interacting with existing equipment requires extra attention. | Ensure existing equipment will comply with project codes and standards and is documented. | Alan Speegle (Southern Co.)
710 | Existing | I&C | I&C | Design | Safety | Interacting with existing equipment requires extra attention. | Ensure the existing equipment and control systems are compatible with the project design. | Alan Speegle (Southern Co.)
711 | Existing | I&C | I&C | Design | Safety | Interacting with existing equipment requires extra attention. | Ensure design for tie-ins will require a minimum of “Hot Work Permits”. | Alan Speegle (Southern Co.)
712 | Existing | I&C | I&C | Design | Safety | Interacting with existing equipment requires extra attention. | Ensure the location of shut-off valves, disconnects and other safety devices are identified and shown on the project drawings. Ensure construction will be allowed to access these locations for emergency situations. | Alan Speegle (Southern Co.)
713 | Existing | I&C | I&C | Design | Safety | Interacting with existing equipment requires extra attention. | Ensure the name, position, telephone and other necessary information is maintained in the project of individual contacts for existing tie-ins and/or equipment information. | Alan Speegle (Southern Co.)
714 | Fire Hazards | I&C | I&C | Design | Safety | Avoid potential fire harzards and exit obstructions. | Ensure equipment electrical cables, wiring and conduit are routed to avoid potential fire hazards. | Alan Speegle (Southern Co.)
715 | Fire Hazards | I&C | I&C | Design | Safety | Avoid potential fire harzards and exit obstructions. | Ensure instruments/devices are not located as to obstruct exists. | Alan Speegle (Southern Co.)
716 | Freeze Protection | I&C | I&C | Design | Safety | Freeze protection notification for project requirements. | Ensure equipment requiring freeze protection have been identified and shown on the project drawings. Ensure items are indicated on the piping & instrument diagrams. Ensure electrical department are aware of power requirements. | Alan Speegle (Southern Co.)
717 | Freeze Protection | I&C | I&C | Design | Safety | Freeze protection notification for project requirements. | Ensure equipment enclosures, panels, or cabinets contain adequate insulation, heaters, and controls to prevent damage to equipment from freezing. | Alan Speegle (Southern Co.)
718 | Freeze Protection | I&C | I&C | Design | Safety | Freeze protection notification for project requirements. | Ensure the blow-down and shut-off valves are external to the equipment enclosures. | Alan Speegle (Southern Co.)
719 | Freeze Protection | I&C | I&C | Design | Safety | Freeze protection notification for project requirements. | Ensure internal temperature indications are visible from the outside of freeze protection enclosures. | Alan Speegle (Southern Co.)
720 | Grounding | I&C | I&C | Design | Safety | Ground devices at only one point to avoid a ground loop issue. | Ensure instrument ground connections are only at one point within the loop. | Alan Speegle (Southern Co.)
721 | Installation | I&C | I&C | Design | Safety | Ensure that adequate information is available on project drawings to avoid installation problems and issues | Ensure adequate information is available for installation of all instrumentation associated with the project. | Alan Speegle (Southern Co.)
722 | Lightning Protection | I&C | I&C | Design | Safety | Lightning Codes and Standards. | Ensure instrument/devices are adequately protected from lightning damage and in compliance with codes and standards. Design for transient suppressers at transmitters. Identify ground sources and eliminate sensors. | Alan Speegle (Southern Co.)
723 | Lightning Protection | I&C | I&C | Design | Safety | Lightning Codes and Standards. | Ensure the Standard for the Installation of Lightning Protections Systems NFPA-780 has been reviewed. | Alan Speegle (Southern Co.)
724 | Location | I&C | I&C | Design | Safety | Instruments must meet area classifications, be accessible, be visible, and avoid interference hazards. | Ensure instruments/devices are accessible from grade, floors or platforms. | Alan Speegle (Southern Co.)
725 | Location | I&C | I&C | Design | Safety | Instruments must meet area classifications, be accessible, be visible, and avoid interference hazards. | Ensure the location of the root valves and blow-down valves are visible and located accessible from grade, floors or platforms and valve discharges will be prevented from splashing or direct spray on the operator or equipment. | Alan Speegle (Southern Co.)
726 | Location | I&C | I&C | Design | Safety | Instruments must meet area classifications, be accessible, be visible, and avoid interference hazards. | Ensure the equipment is located in an area away from possible leaking conditions. Ensure instrument/devices are not located under or near process lines that could leak and contaminate the equipment. | Alan Speegle (Southern Co.)
727 | Location | I&C | I&C | Design | Safety | Instruments must meet area classifications, be accessible, be visible, and avoid interference hazards. | Ensure transmitters are located as close as possible to the process line connections. Locations of transmitters/devices are shown on the Instrument Location Drawings. Process line connections are shown on the piping isometrics and/or piping layout drawi | Alan Speegle (Southern Co.)
728 | Location | I&C | I&C | Design | Safety | Instruments must meet area classifications, be accessible, be visible, and avoid interference hazards. | Ensure access ways are free from obstructions, tripping and interference hazards. | Alan Speegle (Southern Co.)
729 | Location | I&C | I&C | Design | Safety | Instruments must meet area classifications, be accessible, be visible, and avoid interference hazards. | Ensure equipment is designed and located with a minimum requirement of pipe and accessories disassembly for maintenance and operation. Instrument arrangement shall allow for the removal of a sensor/detector head while maintaining the integrity of the oth | Alan Speegle (Southern Co.)
730 | Location | I&C | I&C | Design | Safety | Instruments must meet area classifications, be accessible, be visible, and avoid interference hazards. | Ensure instruments/devices requiring visible indication are located in an illuminated area at a height and angle for adequate viewing. | Alan Speegle (Southern Co.)
731 | Location | I&C | I&C | Design | Safety | Instruments must meet area classifications, be accessible, be visible, and avoid interference hazards. | Ensure instruments/devices are located in well ventilated areas. | Alan Speegle (Southern Co.)
732 | Location | I&C | I&C | Design | Safety | Instruments must meet area classifications, be accessible, be visible, and avoid interference hazards. | Ensure adequate access to controls for ease of operation and maintenance. | Alan Speegle (Southern Co.)
733 | Materials | I&C | I&C | Design | Safety | Instruments must meet project compatibility standards. | Ensure instruments/devices meet the environmental, process and work site conditions. | Alan Speegle (Southern Co.)
734 | Materials | I&C | I&C | Design | Safety | Instruments must meet project compatibility standards. | Ensure instruments/devices meet the piping specification design issued for the project. All in-line elements that requires flanges shall follow the piping classification and specification. | Alan Speegle (Southern Co.)
735 | Materials | I&C | I&C | Design | Safety | Instruments must meet project compatibility standards. | Ensure instrument/devices are designed to be compatible with fluid and are in compliance with project codes and standards. Ensure instrument/device material (gaskets, diaphragms, o-rings, etc) that comes in contact with hazardous, corrosive or contaminat | Alan Speegle (Southern Co.)
736 | Materials | I&C | I&C | Design | Safety | Instruments must meet project compatibility standards. | Ensure instrument/device are not design to contain asbestos or other known hazardous substances. | Alan Speegle (Southern Co.)
737 | Mechanical | I&C | I&C | Design | Safety | Root Valves connections must be compatible with instrument connections. | Ensure root (shut-off) valves and instrument/device connections match and are adequate to meet the requirements for the project. | Alan Speegle (Southern Co.)
738 | Package Supplied Units | I&C | I&C | Design | Safety | Vendor supplied equipment must be project specific and be maintianed. | Ensure package suppliers have terminated instrument connections at the edge of the package edge in bulkhead connectors or junction boxes. | Alan Speegle (Southern Co.)
739 | Package Supplied Units | I&C | I&C | Design | Safety | Vendor supplied equipment must be project specific and be maintianed. | Ensure package suppliers design agrees and is in compliance with project codes and standards. | Alan Speegle (Southern Co.)
740 | Panels | I&C | I&C | Design | Safety | New and existing panels and consoles must be in compliances with project scope and requirements. | Ensure spacing between panels are in compliances with project codes and standards. | Alan Speegle (Southern Co.)
741 | Panels | I&C | I&C | Design | Safety | New and existing panels and consoles must be in compliances with project scope and requirements. | Ensure existing panels are adequate for project and meets the project codes and standards requirements. | Alan Speegle (Southern Co.)
742 | Piping | I&C | I&C | Design | Safety | Avoid thermal problems with piping and tubing expansion. | Ensure that piping subject to thermal growth are compensated for. | Alan Speegle (Southern Co.)
743 | Piping | I&C | I&C | Design | Safety | Avoid thermal problems with piping and tubing expansion. | Ensure expansion loops are designed for high temperature applications. Loop seal or siphon will protect steam pressure sensing devices that must be mounted above the process connections. | Alan Speegle (Southern Co.)
744 | Piping | I&C | I&C | Design | Safety | Avoid thermal problems with piping and tubing expansion. | Ensure insulation and/or heat tracing have been provided in the design. | Alan Speegle (Southern Co.)
745 | Piping | I&C | I&C | Design | Safety | Avoid thermal problems with piping and tubing expansion. | Ensure instrument connections and shutoff valves are accessible. | Alan Speegle (Southern Co.)
746 | Power | I&C | I&C | Design | Safety | Communicate power requirements as soon as possible. | Ensure power requirements are communicated to the electrical design department. | Alan Speegle (Southern Co.)
747 | Process Conditions | I&C | I&C | Design | Safety | Instrument and controls compatibility. | Ensure thermowells are designed, calculated and specified for the process applications. | Alan Speegle (Southern Co.)
748 | Process Conditions | I&C | I&C | Design | Safety | Instrument and controls compatibility. | Ensure instruments/devices are within the design range listed on the mechanical equipment specifications. | Alan Speegle (Southern Co.)
749 | Process Hazard Analysis (PHA) | I&C | I&C | Design | Safety | Document Process Hazard Analysis. | Ensure instruments & controls documentation is provided for the project Process Hazard Analysis. | Alan Speegle (Southern Co.)
750 | Safety | I&C | I&C | Design | Safety | Review Personal Protective Equipment. | Ensure insulation and barriers are design into the system to provide personnel protection. | Alan Speegle (Southern Co.)
751 | Safety | I&C | I&C | Design | Safety | Review Personal Protective Equipment. | Ensure design will allow construction to maintain a neat, clean work area within the instruments & controls design area. | Alan Speegle (Southern Co.)
752 | Safety | I&C | I&C | Design | Safety | Review Personal Protective Equipment. | Ensure design personnel are trained for the project site and familiar with site procedures and requirements. Employees will be trained and will wear only company approved Personal Protective Equipment (PPE). Employees will wear eye protection that meets | Alan Speegle (Southern Co.)
753 | Safety | I&C | I&C | Design | Safety | Review Personal Protective Equipment. | Ensure proper location of warning signs to alert of hazards. | Alan Speegle (Southern Co.)
754 | Safety | I&C | I&C | Design | Safety | Review Personal Protective Equipment. | Ensure safety showers and eye wash stations are according to codes and standards. Safety showers and eye wash stations will be freeze protected and will incorporate alarms. | Alan Speegle (Southern Co.)
755 | Site Hazards | I&C | I&C | Design | Safety | Ensure that individuals are aware of any potential site hazard. | Ensure potential hazards are communicated to construction and contractors. | Alan Speegle (Southern Co.)
756 | Site Hazards | I&C | I&C | Design | Safety | Ensure that individuals are aware of any potential site hazard. | Ensure design personnel are familiar with site hazards associated with the project. Employees will be familiar with plant site hazard communication. Employees will be familiar with plant site toxic & hazardous substances. Employees will be familiar with | Alan Speegle (Southern Co.)
757 | Site Hazards | I&C | I&C | Design | Safety | Ensure that individuals are aware of any potential site hazard. | Ensure design personnel are familiar with plant site evaluation instructions. | Alan Speegle (Southern Co.)
758 | Supports | I&C | I&C | Design | Safety | Instrument supports to structural steel. | Ensure instruments/devices requiring structural steel for mounting is designed to prevent any cutting, drilling, or bending of the structural steel. | Alan Speegle (Southern Co.)
759 | Supports | I&C | I&C | Design | Safety | Instrument supports to structural steel. | Ensure instruments/devices requiring structural steel, equipment, or structural members for mounting and support of the instrument/devices does not require structural steel/members or equipment removal for frequent instrument/device maintenance. | Alan Speegle (Southern Co.)
760 | Supports | I&C | I&C | Design | Safety | Instrument supports to structural steel. | Ensure instrument/devices mounted on structural steel are not subject to vibration or movement. | Alan Speegle (Southern Co.)
761 | Testing | I&C | I&C | Design | Safety | Test equipment and tools, procedures, reports and test connections. | Ensure test equipment and tools needed to support equipment are specified for the project. | Alan Speegle (Southern Co.)
762 | Testing | I&C | I&C | Design | Safety | Test equipment and tools, procedures, reports and test connections. | Ensure testing procedures are provided and in compliance with codes and standards. | Alan Speegle (Southern Co.)
763 | Testing | I&C | I&C | Design | Safety | Test equipment and tools, procedures, reports and test connections. | Ensure equipment test reports are generated and filed in project file. | Alan Speegle (Southern Co.)
764 | Testing | I&C | I&C | Design | Safety | Test equipment and tools, procedures, reports and test connections. | Ensure performance test connections are indicated on design documents and are accessible. | Alan Speegle (Southern Co.)
765 | Tubing | I&C | I&C | Design | Safety | Instrument tubing issues. | Ensure tubing material is adequate for the process temperature and pressure. For temperature exceeding 900 degrees F, ensure that 316H Stainless Steel tubing is specified. (Reference ASME B31.1). | Alan Speegle (Southern Co.)
766 | Tubing | I&C | I&C | Design | Safety | Instrument tubing issues. | Ensure all tubing complies with and is accordance with ANSI/ISA-S77.70, Fossil Fuel Power Plant Instrument Piping Installation. Ensure all tubing is specified, designed, ordered, and received with “Minimum Wall Thickness” designation. | Alan Speegle (Southern Co.)
767 | Tubing | I&C | I&C | Design | Safety | Instrument tubing issues. | Ensure tube fitting for any steam services above 600 PSIG are designed for welded construction. | Alan Speegle (Southern Co.)
768 | Tubing | I&C | I&C | Design | Safety | Instrument tubing issues. | Ensure design of tubing, fittings, and tubing connections are minimized. | Alan Speegle (Southern Co.)
769 | Tubing | I&C | I&C | Design | Safety | Instrument tubing issues. | Ensure tubing subject to thermal growth are compensated for. | Alan Speegle (Southern Co.)
770 | Tubing | I&C | I&C | Design | Safety | Instrument tubing issues. | Ensure expansion loops are designed for high temperature applications. | Alan Speegle (Southern Co.)
771 | Tubing | I&C | I&C | Design | Safety | Instrument tubing issues. | Ensure insulation and/or heat tracing have been provided in the design. | Alan Speegle (Southern Co.)
772 | Tubing | I&C | I&C | Design | Safety | Instrument tubing issues. | Ensure tubing is not routed in the same tray as electrical wiring and cable. | Alan Speegle (Southern Co.)
773 | Tubing | I&C | I&C | Design | Safety | Instrument tubing issues. | Ensure foreign equipment have been reviewed for compatibility with connections, material, operation, and maintenance. | Alan Speegle (Southern Co.)
774 | Tubing | I&C | I&C | Design | Safety | Instrument tubing issues. | Ensure copper tubing is not allowed in ammonia services. | Alan Speegle (Southern Co.)
775 | Valves | I&C | I&C | Design | Safety | Root valves, blow-down valves, control valves and compatibility. | Ensure valve accessories (positioners, solenoid valves, position switches, etc) have been reviewed, evaluated, specified, and located to be accessible for the operation and maintenance of the control valve. | Alan Speegle (Southern Co.)
776 | Valves | I&C | I&C | Design | Safety | Root valves, blow-down valves, control valves and compatibility. | Ensure valve accessories are compatible with the control systems. | Alan Speegle (Southern Co.)
777 | Valves | I&C | I&C | Design | Safety | Root valves, blow-down valves, control valves and compatibility. | Ensure double valving for piping and tubing are met for any service above 600 PSIG. | Alan Speegle (Southern Co.)
778 | Valves | I&C | I&C | Design | Safety | Root valves, blow-down valves, control valves and compatibility. | Ensure that each pressure instrument with process connection shall have individual process isolation valves. | Alan Speegle (Southern Co.)
779 | Testing | Civil; Mechanical | Concrete | Design | Safety | Timely testing of materials, structural members, and project systems is essential to prevent collapse of the structure or injury during construction. | Require concrete test results to be verified before elevated form stripping and removal of shoring. | Alan Speegle (Southern Co.)
780 | Testing | Civil; Mechanical | Concrete | Design | Safety | Timely testing of materials, structural members, and project systems is essential to prevent collapse of the structure or injury during construction. | Specify the use of testing devices which are embedded in concrete members in order to test the strength of the concrete before form removal. | Alan Speegle (Southern Co.)
781 | Testing | Civil; Mechanical | Concrete | Design | Safety | Timely testing of materials, structural members, and project systems is essential to prevent collapse of the structure or injury during construction. | Specify testing procedures for complicated designs or specialized mechanical, electrical, or piping systems. | Alan Speegle (Southern Co.)
782 | Caissons | Civil | Concrete | Design | Safety | Pile foundation systems which are not designed with consideration of the soil conditions and pile driving equipment can lead to cave-in and other hazards for construction workers. | To prevent cave-ins due to vibration of loose soil, do not use driven piles in deep excavations in areas of loose or backfilled soil. | Alan Speegle (Southern Co.)
783 | Caissons | Civil | Concrete | Design | Safety | Pile foundation systems which are not designed with consideration of the soil conditions and pile driving equipment can lead to cave-in and other hazards for construction workers. | Avoid designing piles at angles flatter than 4:12 (horizontal:vertical). | Alan Speegle (Southern Co.)
784 | Caissons | Civil | Concrete | Design | Safety | Pile foundation systems which are not designed with consideration of the soil conditions and pile driving equipment can lead to cave-in and other hazards for construction workers. | Take heave into account when locating piles. | Alan Speegle (Southern Co.)
785 | Caissons | Civil | Concrete | Design | Safety | Pile foundation systems which are not designed with consideration of the soil conditions and pile driving equipment can lead to cave-in and other hazards for construction workers. | Each caisson rock socket needs to be inspected for competent rock soundness at the bottom | Alan Speegle (Southern Co.)
786 | Foundations | Civil | Concrete | Design | Safety | Footing location and reinforcing steel can create collapse, tripping, and fall hazards for construction workers during the construction of the foundation. | Use red dye concrete to encase underground utility duct runs. | Alan Speegle (Southern Co.)
787 | Foundations | Civil | Concrete | Design | Safety | Footing location and reinforcing steel can create collapse, tripping, and fall hazards for construction workers during the construction of the foundation. | When practical, design bottom of foundation to have the same elevation. | Alan Speegle (Southern Co.)
788 | Foundations | Civil | Concrete | Design | Safety | Footing location and reinforcing steel can create collapse, tripping, and fall hazards for construction workers during the construction of the foundation. | When developing a plot plan, group footings in a way that permits proper drainage of mass excavations. | Alan Speegle (Southern Co.)
789 | Foundations | Civil | Concrete | Design | Safety | Footing location and reinforcing steel can create collapse, tripping, and fall hazards for construction workers during the construction of the foundation. | Locate new footings away from existing foundations. | Alan Speegle (Southern Co.)
790 | Foundations | Civil | Concrete | Design | Safety | Footing location and reinforcing steel can create collapse, tripping, and fall hazards for construction workers during the construction of the foundation. | Some contractors may want to use 4" x 4" mat mesh or WWF on top of 12"spaced top rebar to provide a walking surface for the concrete workers. | Alan Speegle (Southern Co.)
791 | Foundations | Civil | Concrete | Design | Safety | Footing location and reinforcing steel can create collapse, tripping, and fall hazards for construction workers during the construction of the foundation. | Review clearances between forms, anchor bolts, sleeves, and rebar at congested pier locations to ensure that there is sufficient room for concrete placing and consolidating equipment. | Alan Speegle (Southern Co.)
792 | Foundations | Civil | Concrete | Design | Safety | Footing location and reinforcing steel can create collapse, tripping, and fall hazards for construction workers during the construction of the foundation. | Standardize anchor bolts to several different diameters, types and lengths. | Alan Speegle (Southern Co.)
793 | Foundations | Civil | Concrete | Design | Safety | Footing location and reinforcing steel can create collapse, tripping, and fall hazards for construction workers during the construction of the foundation. | When you review concrete mix, make sure the aggregate specified type and size reflects material the supplier intends to use. | Alan Speegle (Southern Co.)
794 | Foundations | Civil | Concrete | Design | Safety | Footing location and reinforcing steel can create collapse, tripping, and fall hazards for construction workers during the construction of the foundation. | When you review concrete mix, make sure the proper curing compound is specified for outside or enclosed conditions. | Alan Speegle (Southern Co.)
795 | Foundations | Civil | Concrete | Design | Safety | Footing location and reinforcing steel can create collapse, tripping, and fall hazards for construction workers during the construction of the foundation. | Before releasing concrete specification review mandatory requirements and optional requirements in ACI 301. | Alan Speegle (Southern Co.)
796 | Foundations | Civil | Concrete | Design | Safety | Footing location and reinforcing steel can create collapse, tripping, and fall hazards for construction workers during the construction of the foundation. | Equipment mounted on skids make the design and installation of the anchor bolts and foundation easier. | Alan Speegle (Southern Co.)
797 | Foundations | Civil | Concrete | Design | Safety | Footing location and reinforcing steel can create collapse, tripping, and fall hazards for construction workers during the construction of the foundation. | Where possible attempt to have rows of similar foundations (example: pumps or blowers) designed to have a single common raft foundation. This will reduce formwork, rebar, and construction manhours. | Alan Speegle (Southern Co.)
798 | Foundations | Civil | Concrete | Design | Safety | Footing location and reinforcing steel can create collapse, tripping, and fall hazards for construction workers during the construction of the foundation. | Approve or specify, in large foundations, the use of maximum size of aggregate to minimize the cement requirements and heat of hydration. | Alan Speegle (Southern Co.)
799 | Foundations | Civil | Concrete | Design | Safety | Footing location and reinforcing steel can create collapse, tripping, and fall hazards for construction workers during the construction of the foundation. | Standardize foundation sizes for pumps, piperacks, structures, and miscellaneous supports. | Alan Speegle (Southern Co.)
800 | Foundations | Civil | Concrete | Design | Safety | Footing location and reinforcing steel can create collapse, tripping, and fall hazards for construction workers during the construction of the foundation. | Extend foundations dimension 12" to allow setting wall forms on concrete slab. | Alan Speegle (Southern Co.)
801 | Foundations | Civil | Concrete | Design | Safety | Footing location and reinforcing steel can create collapse, tripping, and fall hazards for construction workers during the construction of the foundation. | Design foundations to be placed directly against earth, instead of forming, where soil, site and structural conditions permit. | Alan Speegle (Southern Co.)
802 | Foundations | Civil | Concrete | Design | Safety | Footing location and reinforcing steel can create collapse, tripping, and fall hazards for construction workers during the construction of the foundation. | Design small foundations and slab on grade without haunches. | Alan Speegle (Southern Co.)
803 | Foundations | Civil | Concrete | Design | Safety | Footing location and reinforcing steel can create collapse, tripping, and fall hazards for construction workers during the construction of the foundation. | Eliminate offsets, tapered sections, and other complicated shaped in foundations. | Alan Speegle (Southern Co.)
804 | Foundations | Civil | Concrete | Design | Safety | Footing location and reinforcing steel can create collapse, tripping, and fall hazards for construction workers during the construction of the foundation. | Consider using drilled adhesive or epoxy anchors or drilled mechanical anchors in foundations with small loads. | Alan Speegle (Southern Co.)
805 | Foundations | Civil | Concrete | Design | Safety | Footing location and reinforcing steel can create collapse, tripping, and fall hazards for construction workers during the construction of the foundation. | Consider using anchor bolt sleeve for equipment foundations. | Alan Speegle (Southern Co.)
806 | Foundations | Civil | Concrete | Design | Safety | Footing location and reinforcing steel can create collapse, tripping, and fall hazards for construction workers during the construction of the foundation. | Consider delivery time for hot dipped galvanized or alloy steel anchor bolts or anchor rods. | Alan Speegle (Southern Co.)
807 | Foundations | Civil | Concrete | Design | Safety | Footing location and reinforcing steel can create collapse, tripping, and fall hazards for construction workers during the construction of the foundation. | Provide adequate embedments in concrete foundations, piers and wall for future attachment of platforms, stairs, light fixtures, and etc. | Alan Speegle (Southern Co.)
808 | Foundations | Civil | Concrete | Design | Safety | Footing location and reinforcing steel can create collapse, tripping, and fall hazards for construction workers during the construction of the foundation. | Provide railing or grating on top of sumps. | Alan Speegle (Southern Co.)
809 | Foundations | Civil | Concrete | Design | Safety | Footing location and reinforcing steel can create collapse, tripping, and fall hazards for construction workers during the construction of the foundation. | Epoxy grout will not be used to grout equipment on scrubber project. | Alan Speegle (Southern Co.)
810 | Foundations | Civil | Concrete | Design | Safety | Footing location and reinforcing steel can create collapse, tripping, and fall hazards for construction workers during the construction of the foundation. | Sumps will have steel ladder rungs for access. Steel grating and support steel will be furnished as required to support the pumps and grating. Sumps will be elevated 18-24 inches to keep vehicles off the top of the sump | Alan Speegle (Southern Co.)
811 | Foundations | Civil | Concrete | Design | Safety | Footing location and reinforcing steel can create collapse, tripping, and fall hazards for construction workers during the construction of the foundation. | Sumps ,which contain a potentially corrosive liquid, should consider using a steel rung with protective plastic coating such as the "PS3-PFC" manhole steps by M.A. Industries of Peachtree City, GA. Consider adding a grab bar to enable the person to safel | Alan Speegle (Southern Co.)
812 | Slab On Grade | Civil | Concrete | Design | Safety | Concrete floor finishes and concrete stairway and ladder landings should be designed to prevent falls and obstructions.. | Design and schedule the layout of stairway and ladder concrete landings to be constructed as part of the structure's foundation system. | Alan Speegle (Southern Co.)
813 | Slab On Grade | Civil | Concrete | Design | Safety | Concrete floor finishes and concrete stairway and ladder landings should be designed to prevent falls and obstructions.. | Design and schedule slabs-on-grade, sidewalks, roadways, and other flatwork around elevated structures to be constructed as early as possible and available for use by construction workers. | Alan Speegle (Southern Co.)
814 | Slab On Grade | Civil | Concrete | Design | Safety | Concrete floor finishes and concrete stairway and ladder landings should be designed to prevent falls and obstructions.. | Design the finished floor around mechanical equipment to be at one level (no steps, blockouts, slab depressions, etc.). | Alan Speegle (Southern Co.)
815 | Slab On Grade | Civil | Concrete | Design | Safety | Concrete floor finishes and concrete stairway and ladder landings should be designed to prevent falls and obstructions.. | Keep steps, curbs, blockouts, slab depressions, and other tripping hazards away from window openings, exterior edges, and floor openings. | Alan Speegle (Southern Co.)
816 | Slab On Grade | Civil | Concrete | Design | Safety | Concrete floor finishes and concrete stairway and ladder landings should be designed to prevent falls and obstructions.. | Design the covers over indoor sumps, outlet boxes, drains, etc. to be flush with the finished floor. Design the top of outdoor sumps to be 6" +/- above the top of the slab on grade in areas without vehicular traffic. Top of sumps should be 18" above the | Alan Speegle (Southern Co.)
817 | Slab On Grade | Civil | Concrete | Design | Safety | Concrete floor finishes and concrete stairway and ladder landings should be designed to prevent falls and obstructions.. | Support small equipment on a concrete pad 6" above the finished floor. | Alan Speegle (Southern Co.)
818 | Slab On Grade | Civil; Mechanical | Concrete | Design | Safety | Concrete floor finishes and concrete stairway and ladder landings should be designed to prevent falls and obstructions.. | Route piping drains and overflow outlets to trench drains. | Alan Speegle (Southern Co.)
819 | Slab On Grade | Civil; Mechanical | Concrete | Design | Safety | Concrete floor finishes and concrete stairway and ladder landings should be designed to prevent falls and obstructions.. | Locate drains away from walkways, work areas, and the structure perimeter. | Alan Speegle (Southern Co.)
820 | Slab On Grade | Civil; Mechanical | Concrete | Design | Safety | Concrete floor finishes and concrete stairway and ladder landings should be designed to prevent falls and obstructions.. | Provide drainage for all floor areas, especially around elevated equipment pads. | Alan Speegle (Southern Co.)
821 | Slab On Grade | Civil | Concrete | Design | Safety | Concrete floor finishes and concrete stairway and ladder landings should be designed to prevent falls and obstructions.. | Provide a minimum amount of slope on concrete exterior walkways and platforms to prevent puddling of water. | Alan Speegle (Southern Co.)
822 | Slab On Grade | Civil | Concrete | Design | Safety | Concrete floor finishes and concrete stairway and ladder landings should be designed to prevent falls and obstructions.. | Note on the contract drawings the existing and new floor design loads to aid the constructor in determining material stockpile locations and heavy equipment maneuverability. | Alan Speegle (Southern Co.)
823 | Slab On Grade | Civil | Concrete | Design | Safety | Concrete floor finishes and concrete stairway and ladder landings should be designed to prevent falls and obstructions.. | Design the top layer of floor slab reinforcing to be spaced at no more than 6 inches on center each way to provide a stable, continuous walking surface before placement of the concrete. | Alan Speegle (Southern Co.)
824 | Slab On Grade | Civil | Concrete | Design | Safety | Concrete floor finishes and concrete stairway and ladder landings should be designed to prevent falls and obstructions.. | Specify the required in-place density of subgrade soils for slabs on grade as a percent of the maximum laboratory density. | Alan Speegle (Southern Co.)
825 | Slab On Grade | Civil | Concrete | Design | Safety | Concrete floor finishes and concrete stairway and ladder landings should be designed to prevent falls and obstructions.. | Specify the compaction requirements of the backfill around foundations. Contractor should schedule the completion of the backfilling as soon as possible. | Alan Speegle (Southern Co.)
826 | Slab On Grade | Civil | Concrete | Design | Safety | Concrete floor finishes and concrete stairway and ladder landings should be designed to prevent falls and obstructions.. | Specify broom finish (non-slip walking surfaces) on floors adjacent to open water or exposed to the weather. | Alan Speegle (Southern Co.)
827 | Slab On Grade | Civil | Concrete | Design | Safety | Concrete floor finishes and concrete stairway and ladder landings should be designed to prevent falls and obstructions.. | Containment will be provided around the slurry tanks, JBR, and transformer. | Alan Speegle (Southern Co.)
828 | Slab On Grade | Civil | Concrete | Design | Safety | Concrete floor finishes and concrete stairway and ladder landings should be designed to prevent falls and obstructions.. | Guard posts are required to protect steel bents and structures from trucks or loaders in vehicle access areas. | Alan Speegle (Southern Co.)
829 | Slab On Grade | Civil | Concrete | Design | Safety | Concrete floor finishes and concrete stairway and ladder landings should be designed to prevent falls and obstructions.. | Guard posts are required to protect equipment adjacent to vehicle access areas. | Alan Speegle (Southern Co.)
830 | Slab On Grade | Civil | Concrete | Design | Safety | Concrete floor finishes and concrete stairway and ladder landings should be designed to prevent falls and obstructions.. | U-drain forms will be considered for this project. | Alan Speegle (Southern Co.)
831 | Slab On Grade | Civil | Concrete | Design | Safety | Concrete floor finishes and concrete stairway and ladder landings should be designed to prevent falls and obstructions.. | Containment around Scrubber Island will be concrete curb with provisions for ramp sccess for vehicles in several areas. | Alan Speegle (Southern Co.)
832 | Elevated Floor Concrete | Civil | Concrete | Design | Safety | Concrete: Elevated Floor Concrete | Consider using bent steel form plate on elevated floor slabs around the edge of conrete at large openings and around the perimeter. | Alan Speegle (Southern Co.)
833 | Elevated Floor Concrete | Civil | Concrete | Design | Safety | Concrete: Elevated Floor Concrete | Specify composite steel form deck to eliminate formwork and minimize rebar in elevated slabs. | Alan Speegle (Southern Co.)
834 | Elevated Floor Concrete | Civil | Concrete | Design | Safety | Concrete: Elevated Floor Concrete | Specify the concrete floor finish. | Alan Speegle (Southern Co.)
835 | Elevated Floor Concrete | Civil | Concrete | Design | Safety | Concrete: Elevated Floor Concrete | When specifing a top of concrete elevation, consider the combined steel and concrete tolerance (including deflection). This may influence the beam size, composite design of floor, specifing Ff and Fl numbers for floor flatness and levelness. | Alan Speegle (Southern Co.)
836 | Elevated Floor Concrete | Civil | Concrete | Design | Safety | Concrete: Elevated Floor Concrete | When showing pipe sleeve on drawings, consider if the sleeve will be installed before or after the concrete is placed. | Alan Speegle (Southern Co.)
837 | Formwork | Civil | Concrete | Design | Safety | Concrete: Formwork | Limit the lift height of concrete pours to minimize the load on formwork and the risk of collapse of fresh concrete during pouring operations. | Alan Speegle (Southern Co.)
838 | Formwork | Civil | Concrete | Design | Safety | Concrete: Formwork | Specification should warn contractor about dangers of workers assembling formwork in high wind. | Alan Speegle (Southern Co.)
839 | Formwork | Civil | Concrete | Design | Safety | Concrete: Formwork | Specify on drawings or specifications if calculations and drawings for formwork must be sealed by a licensed engineer. | Alan Speegle (Southern Co.)
840 | Formwork | Civil | Concrete | Design | Safety | Concrete: Formwork | Specify the minimum compressive strength for removal of elevated forms supporting the weight of concrete if different than the specified compressive strength of concrete. | Alan Speegle (Southern Co.)
841 | Formwork | Civil | Concrete | Design | Safety | Concrete: Formwork | Specify if the alternative methods for evaluating concrete strength for formwork removal are permitted. | Alan Speegle (Southern Co.)
842 | Formwork | Civil | Concrete | Design | Safety | Concrete: Formwork | Consider using round piers or columns instead of odd size rectangular columns. This would simplify forming operations and permit the use of disposable tubes. | Alan Speegle (Southern Co.)
843 | Formwork | Civil | Concrete | Design | Safety | Concrete: Formwork | Consider specifing sacrifical formwork, sheet piling and lean concrete below grade so that backfill can be placed before the concrete. | Alan Speegle (Southern Co.)
844 | Formwork | Civil | Concrete | Design | Safety | Concrete: Formwork | Standardize building bay spacing to maximize the using of gang forms on grade beams and walls. | Alan Speegle (Southern Co.)
845 | Formwork | Civil | Concrete | Design | Safety | Concrete: Formwork | Dimension concrete foundations and structures to make the maximum use of commercial forms. | Alan Speegle (Southern Co.)
846 | Formwork | Civil | Concrete | Design | Safety | Concrete: Formwork | Review design of formwork for chimney and JBR foundations. | Alan Speegle (Southern Co.)
847 | Concrete Masonry Units (Concrete Blocks) | Civil | Concrete | Design | Safety | Construction workers can sustain injuries due to repeated lifting of masonry blocks which are heavy, odd-sized, or irregularly shaped. Crowded and confined areas below elevated masonry work increases the risk of workers being struck by falling bricks, ma | Do not specify the use of masonry materials or liquids which contain toxic substances. | Alan Speegle (Southern Co.)
848 | Concrete Masonry Units (Concrete Blocks) | Civil | Concrete | Design | Safety | Construction workers can sustain injuries due to repeated lifting of masonry blocks which are heavy, odd-sized, or irregularly shaped. Crowded and confined areas below elevated masonry work increases the risk of workers being struck by falling bricks, ma | Investigate the hazards associated with the specified construction materials and alert the constructor of the necessary safety precautions. | Alan Speegle (Southern Co.)
849 | Concrete Masonry Units (Concrete Blocks) | Civil | Concrete | Design | Safety | Construction workers can sustain injuries due to repeated lifting of masonry blocks which are heavy, odd-sized, or irregularly shaped. Crowded and confined areas below elevated masonry work increases the risk of workers being struck by falling bricks, ma | Allow for a large, unobstructed, open area (limited access zone) below elevated masonry work to minimize the risk of workers being struck by falling objects. See Section 1926.750 of the Code of Federal Regulations. | Alan Speegle (Southern Co.)
850 | Concrete Masonry Units (Concrete Blocks) | Civil | Concrete | Design | Safety | Construction workers can sustain injuries due to repeated lifting of masonry blocks which are heavy, odd-sized, or irregularly shaped. Crowded and confined areas below elevated masonry work increases the risk of workers being struck by falling bricks, ma | Minimize the size and weight of masonry blocks. | Alan Speegle (Southern Co.)
851 | Concrete Masonry Units (Concrete Blocks) | Civil | Concrete | Design | Safety | Construction workers can sustain injuries due to repeated lifting of masonry blocks which are heavy, odd-sized, or irregularly shaped. Crowded and confined areas below elevated masonry work increases the risk of workers being struck by falling bricks, ma | Use masonry blocks of consistent size and shape. | Alan Speegle (Southern Co.)
852 | Concrete Masonry Units (Concrete Blocks) | Civil | Concrete | Design | Safety | Construction workers can sustain injuries due to repeated lifting of masonry blocks which are heavy, odd-sized, or irregularly shaped. Crowded and confined areas below elevated masonry work increases the risk of workers being struck by falling bricks, ma | On larger masonry blocks, provide cast-in handles or handholds for easy lifting. | Alan Speegle (Southern Co.)
853 | Reinforcing | Civil | Concrete | Design | Safety | The manipulation and erection of reinforcing steel and formwork for reinforced concrete structural members can be hazardous to construction workers. | Specify required grade, types, and sizes. ASTM A 706 is expensive and not readily available. | Alan Speegle (Southern Co.)
854 | Reinforcing | Civil | Concrete | Design | Safety | The manipulation and erection of reinforcing steel and formwork for reinforced concrete structural members can be hazardous to construction workers. | Design concrete members to be of similar size and regularly spaced to facilitate the use, and re-use, of pre-fabricated forms. Consider using shotcrete where conditions warrant. | Alan Speegle (Southern Co.)
855 | Reinforcing | Civil | Concrete | Design | Safety | The manipulation and erection of reinforcing steel and formwork for reinforced concrete structural members can be hazardous to construction workers. | Use a metal deck and concrete fill rather than a slab that requires temporary formwork. | Alan Speegle (Southern Co.)
856 | Reinforcing | Civil | Concrete | Design | Safety | The manipulation and erection of reinforcing steel and formwork for reinforced concrete structural members can be hazardous to construction workers. | Use small sized rebar for framing members at elevated floor levels. Design the rebar such that it can be assembled on the ground and erected in large sections. | Alan Speegle (Southern Co.)
857 | Reinforcing | Civil | Concrete | Design | Safety | The manipulation and erection of reinforcing steel and formwork for reinforced concrete structural members can be hazardous to construction workers. | Show splice location and splice lengths on the drawing. | Alan Speegle (Southern Co.)
858 | Reinforcing | Civil | Concrete | Design | Safety | The manipulation and erection of reinforcing steel and formwork for reinforced concrete structural members can be hazardous to construction workers. | Standardize on a few sizes of rebar such as 5,7, and 10 so that two smaller sizes can be substituted for one larger size. | Alan Speegle (Southern Co.)
859 | Reinforcing | Civil | Concrete | Design | Safety | The manipulation and erection of reinforcing steel and formwork for reinforced concrete structural members can be hazardous to construction workers. | Show vertical wall and pier dowel extenting to 6' height, where practical, instead of using dowels and a vertical bar. | Alan Speegle (Southern Co.)
860 | Reinforcing | Civil | Concrete | Design | Safety | The manipulation and erection of reinforcing steel and formwork for reinforced concrete structural members can be hazardous to construction workers. | If the wall has 2 faces of reinforcing steel, place the horizontal wall rebar on the outside of the vertical bars. This eliminated threading the rebar into position. | Alan Speegle (Southern Co.)
861 | Reinforcing | Civil | Concrete | Design | Safety | The manipulation and erection of reinforcing steel and formwork for reinforced concrete structural members can be hazardous to construction workers. | Discuss with our construction services civil person, the areas we need to specify rebar caps other than dowels and wall vertical bars. | Alan Speegle (Southern Co.)
862 | Specifications | Civil | Concrete | Design | Safety | Concrete: Specifications | Specify and use water-base concrete admixtures. Job site needs access to admixture MSDS. | Alan Speegle (Southern Co.)
863 | Signs, Barricades | Civil | Barricades, Signs, And Warning Devices | Design | Safety | The design and erection sequence of permanent signs can create obstruction and other safety hazards for construction workers. | Design signs with rounded or blunt corners, free of sharp edges, burrs, splinters, and other sharp projections. Orient fasteners so that they do not constitute a safety hazard. | Alan Speegle (Southern Co.)
864 | Signs, Barricades | Civil | Barricades, Signs, And Warning Devices | Design | Safety | The design and erection sequence of permanent signs can create obstruction and other safety hazards for construction workers. | Design and schedule traffic and emergency signs for erection early in the construction phase. | Alan Speegle (Southern Co.)
865 | Signs, Barricades | Civil | Barricades, Signs, And Warning Devices | Design | Safety | The design and erection sequence of permanent signs can create obstruction and other safety hazards for construction workers. | Ensure proper position and location of warning signs to clearly alert workers of hazards. | Alan Speegle (Southern Co.)
866 | Signs, Barricades | Civil | Barricades, Signs, And Warning Devices | Design | Safety | The design and erection sequence of permanent signs can create obstruction and other safety hazards for construction workers. | Signs installed at the plant site should be in English and Spanish or have a picture or diagram to communicate the hazard or safety information. | Alan Speegle (Southern Co.)
867 | Warning Devices | Electrical | Barricades, Signs, And Warning Devices | Design | Safety | Inadequate safety warning devices and signs can lead to safety hazards for construction workers. | Ensure that warning signs, controls, and alarms are standardized throughout the project. | Alan Speegle (Southern Co.)
868 | Warning Devices | Electrical | Barricades, Signs, And Warning Devices | Design | Safety | Inadequate safety warning devices and signs can lead to safety hazards for construction workers. | Ensure that hazardous areas are identified, classified, and provided with adequate boundaries. | Alan Speegle (Southern Co.)
869 | Warning Devices | Electrical; I&C | Barricades, Signs, And Warning Devices | Design | Safety | Inadequate safety warning devices and signs can lead to safety hazards for construction workers. | Provide signs, lights, alarms, etc. to ensure safety near dangerous equipment or areas. | Alan Speegle (Southern Co.)
870 | Warning Devices | Electrical | Barricades, Signs, And Warning Devices | Design | Safety | Inadequate safety warning devices and signs can lead to safety hazards for construction workers. | Provide signs which describe the allowable floor loading. | Alan Speegle (Southern Co.)
871 | Warning Devices | Electrical | Barricades, Signs, And Warning Devices | Design | Safety | Inadequate safety warning devices and signs can lead to safety hazards for construction workers. | Provide emergency showers and eye-wash basins in areas where personnel might come in contact with highly toxic or poisonous materials. | Alan Speegle (Southern Co.)
872 | Warning Devices | Civil | Barricades, Signs, And Warning Devices | Design | Safety | Inadequate safety warning devices and signs can lead to safety hazards for construction workers. | Stencil the capacity of hoist beams | Alan Speegle (Southern Co.)
873 | sound | Civil | Environmental Health | Design | Safety | sound specifications | All continuous, intermittent and impulsive sound levels from 80 decibels to 130 decibels shall be integrated into the noise measurements. | Alan Speegle (Southern Co.)
874 | sound | Civil | Environmental Health | Design | Safety | sound specifications | Instruments used to measure employee noise exposure shall be calibrated to ensure measurement accuracy | Alan Speegle (Southern Co.)
875 | sound | Civil | Environmental Health | Design | Safety | sound specifications | Employees shall be fitted with hearing protection | Alan Speegle (Southern Co.)
876 | worker issues | Civil | Fiberglass | Design | Safety | worker specifications | Each scrubber tank will have a stair. | Alan Speegle (Southern Co.)
877 | worker issues | Civil | Fiberglass | Design | Safety | worker specifications | Fiberglass outlet duct and duct before chimney breaching will have a platform that runs below the expansion joint. One end of the platform will be wide enough to install a 4-foot square scaffold. Platform with short stair will provide access to the man | Alan Speegle (Southern Co.)
878 | worker issues | Civil | Fiberglass | Design | Safety | worker specifications | Caged ladders or stairs are being considered to provide access to the utility bridge at 90 degree turns. Plant personnel will be provided access for equipment maintenance. | Alan Speegle (Southern Co.)
879 | worker issues | Civil | Fiberglass | Design | Safety | worker specifications | Ventilation is required for the temporary metal building over the JBR. (This item is not in the SCGEN engineering scope of work) | Alan Speegle (Southern Co.)
880 | worker issues | Civil | Fiberglass | Design | Safety | worker specifications | Construction workers, plant operations, and construction services personnel need to know the health and fire dangers associated with spraying FRP resins and working around solvent materials. | Alan Speegle (Southern Co.)
881 | fiberglass ground assembly | Civil | Fiberglass | Design | Safety |  | Consider ground assembly of 7 JBR steel roof beams and 6 fiberglass panels. These 8 panel assemblies can be lifted with the steel framing (rigging material) that was used to assemble the panels. | Alan Speegle (Southern Co.)
882 | general | Civil | Fiberglass | Design | Safety |  | Specify communication of hazards, storage requirements of hazardous materials, and disposal and clean-up requirements of hazardous materials. | Alan Speegle (Southern Co.)
883 | general | Civil | Fiberglass | Design | Safety |  | The existing engineering and procurement schedule provides inquiries for anticipated fiberglass shop fabrication. | Alan Speegle (Southern Co.)
884 | Ammonia | I&C | Ammonia | Design | Safety | Design Requirements | Ensure that the Ammonia Detector meets the Performance Requirements set in ISA-92.03.01 | Alan Speegle (Southern Co.)
885 | Ammonia | I&C | Ammonia | Design | Safety | Design Requirements | Ensure that the Ammonia Detectors are installed and maintained as per the requirements in the ISA-RP92.03.02 | Alan Speegle (Southern Co.)
886 | Ammonia | I&C | Ammonia | Design | Safety | Design Requirements | Mount Ammonia Leak Lights and/or Beacons high enough to be visible in the surrounding area. | Alan Speegle (Southern Co.)
887 | Improve safety through use of primary and secondary isolation valves | Mechanical |  | Design | Safety | If an item has an equipment tag it must be isolated and under a Plant Clearence before servicing or any maintenance can be performed. AOV's can not be used as a Clearence isolation valve, they are maintenance items. They are passive process control equipment items. MOV's can be used as isolation valves, but can not be serviced or worked on if they are tagged-out. | Develop P&ID's with Primary and Secondary isolation valves up-stream and down-stream including Clearence vents and Clearence drains of all equipment, ie.. Motor Operated Valves, Air Operated Valves, Orfice Plates, Steam Traps, Strainers, pumps, compressors, instrumentation. All piping designs must support SCG-SH-0200, OSHA CFR 1910.269, and CFR 1910.147. | Alan Speegle (Southern Co.)
888 | Horizontally Supported Tanks | Civil | Ammonia Storage Tank | Design | SafetyQuality | Horizontally mounted ammonia tanks (20,500 gal capacity) should have a pinned saddle support and sliding saddle support. Failure to provide this type of support will produce unevaluated internal stresses in the tank shell and foundation structure. | Provide a Teflon coated plate at the sliding support location. See Crist Unit 6 SCR Ammonia tank foundation for sliding joint detail. See vendor sliding joint data at: http://www.con-servinc.com/csa-b.htm | Alan Speegle (Southern Co.)
889 | Buildings - Coating & Finishes | Mechanical | Buildings - Coating & Finishes | Design | Quality | Buildings - Coating & Finishes | Are architectural painting systems standardized? | Tom Bullington (KBR)
890 | Buildings - Coating & Finishes | Mechanical | Buildings - Coating & Finishes | Design | Quality | Buildings - Coating & Finishes | Are acoustical ceilings, wall coverings, vinyl and ceramic tile standardized?. | Tom Bullington (KBR)
891 | Buildings - Coating & Finishes | Mechanical | Buildings - Coating & Finishes | Design | Quality | Buildings - Coating & Finishes | Is the specification for pipe painting a single color, using labels to identify pipe usage? | Tom Bullington (KBR)
892 | Buildings - Coating & Finishes | Mechanical | Buildings - Coating & Finishes | Design | Quality | Buildings - Coating & Finishes | Are special coatings needing placing prior to installation of equipment identified? | Tom Bullington (KBR)
893 | Buildings - Coordination | Civil | Buildings - Coordination | Design | Quality | Buildings - Coordination | Is the scope interface definition for electrical, instrumentation, piping and mechanical equipment clearly defined in subcontract packages for buildings? | Tom Bullington (KBR)
894 | Buildings - Coordination | Civil | Buildings - Coordination | Design | Quality | Buildings - Coordination | Is the structural steel fabricator supplying the miscellaneous items such as frames for louvers, vents, HVAC supports, clips, etc. that are shown on Architectural drawings and not on Civil/Structural drawings? | Tom Bullington (KBR)
895 | Buildings - Design Considerations | Civil | Buildings - Design Considerations | Design | Quality | Buildings - Design Considerations | Has the project mazimized the use of grating floor systems? | Tom Bullington (KBR)
896 | Buildings - Design Considerations | Civil | Buildings - Design Considerations | Design | Quality | Buildings - Design Considerations | Are building bays standardized wherever possible? | Tom Bullington (KBR)
897 | Buildings - Design Considerations | Civil | Buildings - Design Considerations | Design | Quality | Buildings - Design Considerations | Are door hardwares and fixtures standardized? | Tom Bullington (KBR)
898 | Buildings - Design Considerations | Civil | Buildings - Design Considerations | Design | Quality | Buildings - Design Considerations | Does the substation floor design (embedded channels) support successful roll-in / roll-out of breakers for switchgear? | Tom Bullington (KBR)
899 | Buildings - Design Considerations | Civil | Buildings - Design Considerations | Design | Quality | Buildings - Design Considerations | Is the project using magnetic door seals in lieu of surface mounded adjustable type? | Tom Bullington (KBR)
900 | Buildings - Design Considerations | Civil | Buildings - Design Considerations | Design | Quality | Buildings - Design Considerations | Does the elevation of computer floor (where applicable) is adequately allow cable run tie-ends to equipment? | Tom Bullington (KBR)
901 | Buildings - Design Considerations | Civil | Buildings - Design Considerations | Design | Quality | Buildings - Design Considerations | When referencing codes, be sure to site specifics portions of a code rather than the entire code. | Tom Bullington (KBR)
902 | Buildings - Design Considerations | Civil | Buildings - Design Considerations | Design | Quality | Buildings - Design Considerations | Are multiple design reviews being held to avoid inteferences between HVAC and fire protection / sprinklers? | Tom Bullington (KBR)
903 | Buildings - Design Considerations | Civil | Buildings - Design Considerations | Design | Quality | Buildings - Design Considerations | Can Floor Levels be Standardized? | Tom Bullington (KBR)
904 | Buildings - Design Considerations | Civil | Buildings - Design Considerations | Design | Quality | Buildings - Design Considerations | Is adequate space available in air handler locations to accommodate removal of steam and chilled-water coils? | Tom Bullington (KBR)
905 | Buildings - Design Considerations | Civil | Buildings - Design Considerations | Design | Quality | Buildings - Design Considerations | What checks are being made to ensure ductwork does not interfere with piping and electrical? | Tom Bullington (KBR)
906 | Buildings - Design Considerations | Civil | Buildings - Design Considerations | Design | Quality | Buildings - Design Considerations | Are maintenance requirements being considered when designing HVAC systems. (They are often roof-mounted with poor access and no provisions for hoisting equipment to remove and replace heavy motors and coils). | Tom Bullington (KBR)
907 | Buildings - Design Considerations | Civil | Buildings - Design Considerations | Design | Quality | Buildings - Design Considerations | What design methods are being used to minimize roof penetrations for HVAC ductwork, piping / conduits and structural steel? | Tom Bullington (KBR)
908 | Buildings - Design Considerations | Civil | Buildings - Design Considerations | Design | Quality | Buildings - Design Considerations | What is design considering toprevent coils from freezing when coils are inactive during periods of low temperature. | Tom Bullington (KBR)
909 | Buildings - Design Considerations | Civil | Buildings - Design Considerations | Design | Quality | Buildings - Design Considerations | Have all block-out requirements been completed? Are electrical bus duct locations part of that evaluation? | Tom Bullington (KBR)
910 | Buildings - Scheduling | Admin | Buildings - Scheduling | Project Control | Schedule Performance | Buildings - Scheduling | Is control room rack flooring going to be done early to support the installation of Halon system, DCS and consoles? | Tom Bullington (KBR)
911 | Buildings - Scheduling | Admin | Buildings - Scheduling | Project Control | Schedule Performance | Buildings - Scheduling | Is masonry schedule early in the schedule to allow other trades to begin work sooner? | Tom Bullington (KBR)
912 | Buildings - Scheduling | Admin | Buildings - Scheduling | Project Control | Schedule Performance | Buildings - Scheduling | Are all sprinklers, ductwork, and electrical scheduled for installation prior to suspended ceilings? | Tom Bullington (KBR)
913 | Buildings - Scheduling | Admin | Buildings - Scheduling | Project Control | Schedule Performance | Buildings - Scheduling | Is siding scheduled for procuremnt earlier enough to support building dry-in? | Tom Bullington (KBR)
914 | Buildings - Scheduling | Admin | Buildings - Scheduling | Project Control | Schedule Performance | Buildings - Scheduling | Install roofing scheduled to support building dry-in or earlier? | Tom Bullington (KBR)
915 | Buildings - Scheduling | Admin | Buildings - Scheduling | Project Control | Schedule Performance | Buildings - Scheduling | Will all doors frames (any kind of frames) associated with Masonry construction be ordered and received to avoid any Masonry rework? | Tom Bullington (KBR)
916 | Buildings - Scheduling | Admin | Buildings - Scheduling | Project Control | Schedule Performance | Buildings - Scheduling | When will elevator specification be complete and does it support and early order and delivery of the elevator? | Tom Bullington (KBR)
917 | Buildings - Scheduling | Admin | Buildings - Scheduling | Project Control | Schedule Performance | Buildings - Scheduling | When will lab equipment specification be complete and does it support and early order and delivery of the lab equipment? | Tom Bullington (KBR)
918 | Buildings - Scheduling | Admin | Buildings - Scheduling | Project Control | Schedule Performance | Buildings - Scheduling | Are the recessed mounted toilet accessories scheduled for early delivery? | Tom Bullington (KBR)
919 | Buildings - Scheduling | Admin | Buildings - Scheduling | Project Control | Schedule Performance | Buildings - Scheduling | Are HVAC & Fire Detection on the critical path and does their installation bare directly on the testing of control equipment. Does schedule support the testing schedule? | Tom Bullington (KBR)
920 | Buildings - Scheduling | Admin | Buildings - Scheduling | Project Control | Schedule Performance | Buildings - Scheduling | Is the design of the control rooms, rack rooms, and MCC rooms HVAC scheduled for early release to support the environmental control of these rooms prior to installing DCE and variable speed drive cabinets? | Tom Bullington (KBR)
921 | Buildings - Scheduling | Admin | Buildings - Scheduling | Project Control | Schedule Performance | Buildings - Scheduling | Is the purchase of mounting curbs for rooftop equipment scheduled early enough to allow their installation prior to completion of roof installation. | Tom Bullington (KBR)
922 | Buildings - Scheduling | Admin | Buildings - Scheduling | Project Control | Schedule Performance | Buildings - Scheduling | Are glass and mullion strips specified and order early to support the schedule? These are usually long delivery times. | Tom Bullington (KBR)
923 | Buildings - Scheduling | Admin | Buildings - Scheduling | Project Control | Schedule Performance | Buildings - Scheduling | Do design methods allowinstallation of equipment room walls after placement of large equipment? | Tom Bullington (KBR)
924 | Buildings - Scheduling | Admin | Buildings - Scheduling | Project Control | Schedule Performance | Buildings - Scheduling | Are erection sequences and priorities for off-site shop fabrication of ductwork complete? Implement procedures to monitor the fabricators progress to ensure compliance. | Tom Bullington (KBR)
925 | Buildings - Scheduling | Admin | Buildings - Scheduling | Project Control | Schedule Performance | Buildings - Scheduling | Has the ductwork that must be installed prior to piping and electrical been identified and will be ordered early to aleviate delays or expensive construction? | Tom Bullington (KBR)
926 | Buildings - Wall Openings | Civil | Buildings - Wall Openings | Design | Quality | Buildings - Wall Openings | Do all interior door designs consider accommodating mobile and process equipment in and out of the building? | Tom Bullington (KBR)
927 | Buildings - Wall Openings | Civil | Buildings - Wall Openings | Design | Quality | Buildings - Wall Openings | Consider future maintenance requirements during design of structures, especially fireproof rooms and walls; i.e., use kits for wall penetrations of cables and piping; and access panels and doorways for removal and replacement of equipment. | Tom Bullington (KBR)
928 | Buildings - Wall Openings | Civil | Buildings - Wall Openings | Design | Quality | Buildings - Wall Openings | Layout and detail all of the utility floor, roof and wall penetrations and show on Civil / Architectural drawings. | Tom Bullington (KBR)
929 | Buildings - Wall Openings | Civil | Buildings - Wall Openings | Design | Quality | Buildings - Wall Openings | Review block-out requirements and assure correct location for electrical bus duct locations. | Tom Bullington (KBR)
930 | Civil - Excavation & Backfill | Civil | Civil - Excavation & Backfill | Design | Quality | Civil - Excavation & Backfill | Avoid excavations below the water table when possible. Investigate alternate foundation schemes. | Tom Bullington (KBR)
931 | Civil - Excavation & Backfill | Civil | Civil - Excavation & Backfill | Design | Quality | Civil - Excavation & Backfill | Specify different requirements concerning backfill compaction and maximum lifts for traffic vs. non-traffic areas. | Tom Bullington (KBR)
932 | Civil - Excavation & Backfill | Civil | Civil - Excavation & Backfill | Design | Quality | Civil - Excavation & Backfill | Use geotechnical fabric, granular material, mud mats or lean concrete in the bottom of excavation. | Tom Bullington (KBR)
933 | Civil - Excavation & Backfill | Civil | Civil - Excavation & Backfill | Design | Quality | Civil - Excavation & Backfill | Avoid the use of sheet piling when possible. | Tom Bullington (KBR)
934 | Civil - Excavation & Backfill | Civil | Civil - Excavation & Backfill | Design | Quality | Civil - Excavation & Backfill | Comply with OSHA shoring requirements of excavations during foundation and U/G utility designs. Avoid deep cuts, shoring is expensive. | Tom Bullington (KBR)
935 | Civil - Excavation & Backfill | Civil | Civil - Excavation & Backfill | Design | Quality | Civil - Excavation & Backfill | Establish minimum elevations for excavation. Mass excavate if possible. | Tom Bullington (KBR)
936 | Civil - Grading & Roads | Civil | Civil - Grading & Roads | Design | Quality | Civil - Grading & Roads | Ensures that soil borrow pits and topsoil/spoil stockpile locations are identified early, prior to the civil contract bid. | Tom Bullington (KBR)
937 | Civil - Grading & Roads | Civil | Civil - Grading & Roads | Design | Quality | Civil - Grading & Roads | What drawing are being issued for Fine or Site / grading? | Tom Bullington (KBR)
938 | Civil - Grading & Roads | Civil | Civil - Grading & Roads | Design | Quality | Civil - Grading & Roads | Identify locations for construction water access for site dirt work. | Tom Bullington (KBR)
939 | Civil - Grading & Roads | Civil | Civil - Grading & Roads | Design | Quality | Civil - Grading & Roads | Use permanent roads and drainage to provide good access and mobility during construction. | Tom Bullington (KBR)
940 | Civil - Grading & Roads | Civil | Civil - Grading & Roads | Design | Quality | Civil - Grading & Roads | Provide site water runoff disposal during construction. | Tom Bullington (KBR)
941 | Civil - Grading & Roads | Civil | Civil - Grading & Roads | Design | Quality | Civil - Grading & Roads | Ensure that site work “cut and fill” is balanced. | Tom Bullington (KBR)
942 | Civil - Grading & Roads | Civil | Civil - Grading & Roads | Design | Quality | Civil - Grading & Roads | Identify erosion control requirements to meet local codes, EPA and the Environment Plan requirements. | Tom Bullington (KBR)
943 | Civil - Site Layout & Survey | Civil | Civil - Site Layout & Survey | Design | Quality | Civil - Site Layout & Survey | Establish survey control "permanently" so that when structures are erected, survey control monuments are still accessible. | Tom Bullington (KBR)
944 | Civil - Site Layout & Survey | Civil | Civil - Site Layout & Survey | Design | Quality | Civil - Site Layout & Survey | Issue fence plans early for use in security planning. | Tom Bullington (KBR)
945 | Civil - Site Layout & Survey | Civil | Civil - Site Layout & Survey | Design | Quality | Civil - Site Layout & Survey | Plan layout to gain maximum use of mobile or self-propelled compaction equipment. | Tom Bullington (KBR)
946 | Civil - Underground Pipe & Utilities | Civil | Civil - Underground Pipe & Utilities | Design | Quality | Civil - Underground Pipe & Utilities | Coordinate installation of underground utilities. Develop plan to ensure U/G is complete prior to paving. | Tom Bullington (KBR)
947 | Civil - Underground Pipe & Utilities | Civil | Civil - Underground Pipe & Utilities | Design | Quality | Civil - Underground Pipe & Utilities | Ensure typical sections on detailed drawings show requirements for bedding materials for U/G utilities. | Tom Bullington (KBR)
948 | Civil - Underground Pipe & Utilities | Civil | Civil - Underground Pipe & Utilities | Design | Quality | Civil - Underground Pipe & Utilities | Provide culvert schedule; consider galvanized corrugated or bitumastic coated pipe. | Tom Bullington (KBR)
949 | Civil - Underground Pipe & Utilities | Civil | Civil - Underground Pipe & Utilities | Design | Quality | Civil - Underground Pipe & Utilities | Maximize the use of pre-cast manholes; pull boxes and other miscellaneous concrete items. | Tom Bullington (KBR)
950 | Civil - Underground Pipe & Utilities | Civil | Civil - Underground Pipe & Utilities | Design | Quality | Civil - Underground Pipe & Utilities | Design & coordinate underground work by path of construction schedule. | Tom Bullington (KBR)
951 | Civil - Underground Pipe & Utilities | Civil | Civil - Underground Pipe & Utilities | Design | Quality | Civil - Underground Pipe & Utilities | Use common excavation trenches for U/G piping, direct buried cable and duct banks where possible. | Tom Bullington (KBR)
952 | Civil - Underground Pipe & Utilities | Civil | Civil - Underground Pipe & Utilities | Design | Quality | Civil - Underground Pipe & Utilities | Develop a composite drawing of all underground (foundations, piping and electrical), temporary, new and existing. | Tom Bullington (KBR)
953 | Civil - Underground Pipe & Utilities | Civil | Civil - Underground Pipe & Utilities | Design | Quality | Civil - Underground Pipe & Utilities | Design underground piping, grounding, duct banks and ductwork early enough so that they can be installed during the site work and foundation phase of the project. | Tom Bullington (KBR)
954 | Concrete - Anchor Bolts & Embeds | Civil | Concrete - Anchor Bolts & Embeds | Design | Quality | Concrete - Anchor Bolts & Embeds | When practical, standardize anchor bolts as follows: 1. Specify consistent material, length and thread requirements - 2. Minimize the use of different diameters *Use minimum increments of 1/4" when different diameters are required) and 3. Specify splace and nut in lieu of "J Hook" anchor. | Tom Bullington (KBR)
955 | Concrete - Anchor Bolts & Embeds | Civil | Concrete - Anchor Bolts & Embeds | Design | Quality | Concrete - Anchor Bolts & Embeds | Consider use of drilled/epoxy or drilled/mechanical systems for small anchors (<1") rather than cast-in-place anchor bolts. | Tom Bullington (KBR)
956 | Concrete - Anchor Bolts & Embeds | Civil | Concrete - Anchor Bolts & Embeds | Design | Quality | Concrete - Anchor Bolts & Embeds | Issue anchor bolt lists early, especially if there are requirements for special alloy steel or hot-dipped galvanizing. | Tom Bullington (KBR)
957 | Concrete - Anchor Bolts & Embeds | Civil | Concrete - Anchor Bolts & Embeds | Design | Quality | Concrete - Anchor Bolts & Embeds | Utilize anchor bolt "sleeves" for equipment foundation anchor bolts. | Tom Bullington (KBR)
958 | Concrete - Anchor Bolts & Embeds | Civil | Concrete - Anchor Bolts & Embeds | Design | Quality | Concrete - Anchor Bolts & Embeds | Design embeds flush with face of concrete. | Tom Bullington (KBR)
959 | Concrete - Anchor Bolts & Embeds | Civil | Concrete - Anchor Bolts & Embeds | Design | Quality | Concrete - Anchor Bolts & Embeds | Provide adequate embeds in concrete surfaces for miscellaneous attachments such as doorframes, fire extinguishers and hose reels. | Tom Bullington (KBR)
960 | Concrete - Anchor Bolts & Embeds | Civil | Concrete - Anchor Bolts & Embeds | Design | Quality | Concrete - Anchor Bolts & Embeds | Clearances for anchor bolts and embedded items to be identified on drawings. | Tom Bullington (KBR)
961 | Concrete - Concrete Mixing | Civil | Concrete - Concrete Mixing | Design | Quality | Concrete - Concrete Mixing | Consider early in the project if the amount of concrete in the project warrants an on site Batch Plant. Perform proper inspection if required. | Tom Bullington (KBR)
962 | Concrete - Concrete Mixing | Civil | Concrete - Concrete Mixing | Design | Quality | Concrete - Concrete Mixing | Allow flexibility in concrete design. Designate slump ranges, air content ranges, and do not preclude adding water at the site. | Tom Bullington (KBR)
963 | Concrete - Foundations | Civil | Concrete - Foundations | Design | Quality | Concrete - Foundations | Incorporate small foundations into slab-on-grade design (i.e., surface mounted pads). | Tom Bullington (KBR)
964 | Concrete - Foundations | Civil | Concrete - Foundations | Design | Quality | Concrete - Foundations | Design foundations in congested areas with bottom of concrete at same elevation and use common footings, whenever possible. | Tom Bullington (KBR)
965 | Concrete - Foundations | Civil | Concrete - Foundations | Design | Quality | Concrete - Foundations | Extend slab dimensions 4-inches when placing walls above to accommodate setting outside form on slab. | Tom Bullington (KBR)
966 | Concrete - Foundations | Civil | Concrete - Foundations | Design | Quality | Concrete - Foundations | Whenever structural and site conditions permit, design foundations to allow placement of concrete directly against face of earth, thus eliminating need for forms. | Tom Bullington (KBR)
967 | Concrete - Foundations | Civil | Concrete - Foundations | Design | Quality | Concrete - Foundations | On large equipment foundations, set one anchor bolt 2"+ high to act as a guide pin when setting equipment. | Tom Bullington (KBR)
968 | Concrete - Foundations | Civil | Concrete - Foundations | Design | Quality | Concrete - Foundations | Design foundations and slabs-on-grade without haunches. | Tom Bullington (KBR)
969 | Concrete - Foundations | Civil | Concrete - Foundations | Design | Quality | Concrete - Foundations | Evaluate the use of standard diameter concrete piers and pedestals instead of odd-sized rectangular shapes. | Tom Bullington (KBR)
970 | Concrete - Foundations | Civil | Concrete - Foundations | Design | Quality | Concrete - Foundations | Use straight, flat; easily formed shapes and surfaces instead of offsets, tapered sections, and other complicated concrete shapes. | Tom Bullington (KBR)
971 | Concrete - Foundations | Civil | Concrete - Foundations | Design | Quality | Concrete - Foundations | Standardize building bay dimensions. | Tom Bullington (KBR)
972 | Concrete - Foundations | Civil | Concrete - Foundations | Design | Quality | Concrete - Foundations | Avoid circular foundations for equipment greater than four feet in diameter. Foundation should be octagonal or other easily constructed shape formed by the use of standard forms. | Tom Bullington (KBR)
973 | Concrete - Foundations | Civil | Concrete - Foundations | Design | Quality | Concrete - Foundations | Standardize foundation sizes for pumps, pipe racks, structures and miscellaneous supports. | Tom Bullington (KBR)
974 | Concrete - Foundations | Civil | Concrete - Foundations | Design | Quality | Concrete - Foundations | Dimension concrete foundations and structures to make the maximum use of commercial form sizes. | Tom Bullington (KBR)
975 | Concrete - Foundations | Civil | Concrete - Foundations | Design | Quality | Concrete - Foundations | Provide estimated take-off for each structure, foundation, etc., for each individual drawing. | Tom Bullington (KBR)
976 | Concrete - Foundations | Civil | Concrete - Foundations | Design | Quality | Concrete - Foundations | Place foundation early in project schedule to permit ease of concrete placement. Subsequent underground piping and ducts will eliminate free access. | Tom Bullington (KBR)
977 | Concrete - Foundations | Civil | Concrete - Foundations | Design | Quality | Concrete - Foundations | Use Concrete Maturity Method of Testing concrete in lieu of conventional cylinders. | Tom Bullington (KBR)
978 | Concrete - Piles & Piers | Civil | Concrete - Piles & Piers | Design | Quality | Concrete - Piles & Piers | Investigate costs for different types of deep foundations; i.e., caissons, H-piles, pipe, DeWaul, auger cast or precast concrete piles | Tom Bullington (KBR)
979 | Concrete - Precast Concrete | Civil | Concrete - Precast Concrete | Design | Quality | Concrete - Precast Concrete | Maximize the use of pre-cast manholes, pull boxes and other miscellaneous concrete items. | Tom Bullington (KBR)
980 | Concrete - Precast Concrete | Civil | Concrete - Precast Concrete | Design | Quality | Concrete - Precast Concrete | Design concrete structure to allow pre-cast construction where cost or schedule savings are possible. | Tom Bullington (KBR)
981 | Concrete - Rebar | Civil | Concrete - Rebar | Design | Quality | Concrete - Rebar | Eliminate the use of different grades of rebar. | Tom Bullington (KBR)
982 | Concrete - Rebar | Civil | Concrete - Rebar | Design | Quality | Concrete - Rebar | Reduce the number of reinforcing steel bars in a given concrete placement by using larger bar sizes and thus increasing the required spacing. | Tom Bullington (KBR)
983 | Concrete - Rebar | Civil | Concrete - Rebar | Design | Quality | Concrete - Rebar | Utilize wire mesh (WWF) (flat sheets) for area paving reinforcing instead of rebar where design allows or fiber concrete. | Tom Bullington (KBR)
984 | Concrete - Roads & Paving | Civil | Concrete - Roads & Paving | Design | Quality | Concrete - Roads & Paving | Include permanent plant roads and area paving in the vicinity of pipe ways and other heavily trafficked areas in Site Preparation package for early construction. | Tom Bullington (KBR)
985 | Concrete - Roads & Paving | Civil | Concrete - Roads & Paving | Design | Quality | Concrete - Roads & Paving | Detail and provide for concrete approach aprons at site entrance and include in the Site Preparation Package. | Tom Bullington (KBR)
986 | Concrete - Roads & Paving | Civil | Concrete - Roads & Paving | Design | Quality | Concrete - Roads & Paving | Utilize metal zip strips for bulkheads and eliminate wood forming for area paving joints. | Tom Bullington (KBR)
987 | Construction - Concrete | Civil | Construction - Concrete | Construction | Quality | Construction - Concrete | Maximize concrete contraction joint sawing production. Use lightweight "Soft Cut" electric joint saw while concrete is still very green. | Tom Bullington (KBR)
988 | Construction - Concrete | Civil | Construction - Concrete | Construction | Quality | Construction - Concrete | Follow manufacturer's instructions closely concerning installation and storage of grouting materials. Be aware of remaining shelf life of product. | Tom Bullington (KBR)
989 | Construction - Concrete | Civil | Construction - Concrete | Construction | Quality | Construction - Concrete | Develop a slurry mix of sand and cement to facilitate backfill around congested areas. | Tom Bullington (KBR)
990 | Construction - Concrete | Civil | Construction - Concrete | Construction | Quality | Construction - Concrete | Use anchor bolt/base plate templates from vessel fabricator (vessels 48' & larger) to facilitate accurate placement. | Tom Bullington (KBR)
991 | Construction - Concrete | Civil | Construction - Concrete | Construction | Quality | Construction - Concrete | Design finish paving early; pave only base course and utilize during construction. | Tom Bullington (KBR)
992 | Construction - Electrical | Electrical | Construction - Electrical | Construction | Quality | Construction - Electrical | Plan electrical cable pulling locations for access of equipment, for banking of cable spools and for downhill pulls. | Tom Bullington (KBR)
993 | Construction - Electrical | Electrical | Construction - Electrical | Construction | Quality | Construction - Electrical | Return cable reels promptly for credit. | Tom Bullington (KBR)
994 | Construction - Electrical | Electrical | Construction - Electrical | Construction | Quality | Construction - Electrical | The use of embedded grounding pads inside substation buildings should be installed to ground equipment when possible. | Tom Bullington (KBR)
995 | Construction - Electrical | Electrical | Construction - Electrical | Construction | Quality | Construction - Electrical | Involve key plant E&I maintenance and operation personnel in E&I checkout and start-up planning. | Tom Bullington (KBR)
996 | Construction - Electrical | Electrical | Construction - Electrical | Construction | Quality | Construction - Electrical | Storage requirements and handling procedures should be developed early so that construction can plan for heating, warehouse space requirements on such items as MCCs, switchgear and motors. | Tom Bullington (KBR)
997 | Construction - Equipment | Other | Construction - Equipment | Construction | Quality | Construction - Equipment | Minimize motor vehicle use. Consider using off-road specialty vehicles (four (4) wheeled ATVs or used golf carts) for transport of supervision, tools, and light materials. | Tom Bullington (KBR)
998 | Construction - Equipment | Other | Construction - Equipment | Construction | Quality | Construction - Equipment | Minimize engine-driven welding machine use. Consider using electric eight bank welders or compact individual inverter units. | Tom Bullington (KBR)
999 | Construction - Equipment | Other | Construction - Equipment | Construction | Quality | Construction - Equipment | Minimize separation between welding and weld source. Utilize totable electric inverter welding machines that can be taken directly to the point of work. | Tom Bullington (KBR)
1000 | Construction - Equipment | Other | Construction - Equipment | Construction | Quality | Construction - Equipment | Maximize crane productivity. Consider cranes with load moment indicators and "dial in" spotting capabilities. | Tom Bullington (KBR)
1001 | Construction - Equipment | Other | Construction - Equipment | Construction | Quality | Construction - Equipment | Minimize disruption of adjoining work by sandblasting. Consider using vacuum blasting techniques that recycle grit in a closed system. | Tom Bullington (KBR)
1002 | Construction - Equipment | Other | Construction - Equipment | Construction | Quality | Construction - Equipment | Minimize the use of hand rigging and "bull-rigging" in installing upper level process equipment. Use miniature diesel engine rubber tire deck crane lifted from level to level by ground based cherry picker. Lightweight unit (under 6,000 lbs.) will not overload many equipment decks. Also useful in restricted space application under pipe racks. | Tom Bullington (KBR)
1003 | Construction - Equipment | Other | Construction - Equipment | Construction | Quality | Construction - Equipment | Base selection of construction equipment on versatility, ease of maintenance and simplicity of operation. Consider use of lifts instead of scaffolding. | Tom Bullington (KBR)
1004 | Construction - Equipment | Other | Construction - Equipment | Construction | Quality | Construction - Equipment | Define permanent system equipment that can be used for temporary power (i.e., transformers, lighting panels, and yard lighting). | Tom Bullington (KBR)
1005 | Construction - Equipment | Other | Construction - Equipment | Construction | Quality | Construction - Equipment | Consider use of mobile light plants to provide or supplement area lighting during construction. Look at purchase versus rental and turnover to maintenance at the end of the project. | Tom Bullington (KBR)
1006 | Construction - Material | Other | Construction - Material | Construction | Quality | Construction - Material | Maintain in stock items for bulk materials commodities.(maxi-min stock supply) | Tom Bullington (KBR)
1007 | Construction - Piping | Mechanical | Construction - Piping | Construction | Quality | Construction - Piping | Insure the compressor piping hold-downs are installed per piping detail and bolts are not over tightened. | Tom Bullington (KBR)
1008 | Construction - Piping | Mechanical | Construction - Piping | Construction | Quality | Construction - Piping | Insure the correct type of hold-down is installed in the correct location. There are (3) types, which are hole, slotted hole and long slotted hole. | Tom Bullington (KBR)
1009 | Construction - Piping | Mechanical | Construction - Piping | Construction | Quality | Construction - Piping | Piping guides and anchors - The clearance gaps need to be correct, which is the gap between the edge of the shoe and the guide or anchor. | Tom Bullington (KBR)
1010 | Construction - Piping | Mechanical | Construction - Piping | Construction | Quality | Construction - Piping | Deluge sub-contractor should be reviewed early and often to insure a quality built system. | Tom Bullington (KBR)
1011 | Construction - Piping | Mechanical | Construction - Piping | Construction | Quality | Construction - Piping | Guides on vertical lines have a specific clearance allowance on the sides and back of shoes. Engineering could design the guiding support steel to be more easily adjustable, if shoes or steel are not square. | Tom Bullington (KBR)
1012 | Construction - Safety | Other | Construction - Safety | Construction | Safety | Construction - Safety | Ensure design and inspection of temporary power complies with OSHA and NEC standards, i.e., color coding of wire. | Tom Bullington (KBR)
1013 | Construction - Safety | Other | Construction - Safety | Construction | Safety | Construction - Safety | Ensure that ground fault protection is installed on all temporary power installations, or perform monthly safety inspections of these installations. | Tom Bullington (KBR)
1014 | Construction - Safety | Other | Construction - Safety | Construction | Safety | Construction - Safety | Keep welding leads and extension cords out of walkways by: Locating power distribution panels close to the work areas; Use "Christmas Trees" to keep welding leads and extension cords off of the floor; Use stackable welding machine and Use permanently installed welding outlets. | Tom Bullington (KBR)
1015 | Construction - Safety | Other | Construction - Safety | Construction | Safety | Construction - Safety | Are safety requirements clearly defined and an incentive scheme developed? | Tom Bullington (KBR)
1016 | Construction - Safety | Other | Construction - Safety | Construction | Safety | Construction - Safety | Inspection for safety should comply with OSHA and NEC standards, i.e., color coding of wire. | Tom Bullington (KBR)
1017 | Construction - Safety | Other | Construction - Safety | Construction | Safety | Construction - Safety | Consider the need for special protective equipment and clothing. | Tom Bullington (KBR)
1018 | Construction - Staff Responsibility | Other | Construction - Staff Responsibility | Construction | Quality | Construction - Staff Responsibility | Review project Contract for commissioning, start-up and performance test requirements. | Tom Bullington (KBR)
1019 | Construction - Staff Responsibility | Other | Construction - Staff Responsibility | Construction | Quality | Construction - Staff Responsibility | Verify that care, custody and control transfer procedures are defined in the Contract. | Tom Bullington (KBR)
1020 | Construction - Staff Responsibility | Other | Construction - Staff Responsibility | Construction | Quality | Construction - Staff Responsibility | Ensure that the Contract addresses or defines use of permanent plant operators during commissioning, start-up, and performance testing of the plant. | Tom Bullington (KBR)
1021 | Construction - Staff Responsibility | Other | Construction - Staff Responsibility | Construction | Quality | Construction - Staff Responsibility | Ensure that the Contract addresses the ramifications of premature plant takeover by [Client] before contractual care, custody and control transfer. | Tom Bullington (KBR)
1022 | Construction - Staff Responsibility | Other | Construction - Staff Responsibility | Construction | Quality | Construction - Staff Responsibility | Review Contract for methods of resolving [Client] disputes over commissioning, start-up and performance testing issues. | Tom Bullington (KBR)
1023 | Construction - Staff Responsibility | Other | Construction - Staff Responsibility | Construction | Quality | Construction - Staff Responsibility | Develop an interface document / matrix between Engineering, Construction, Start-up to better define each group's roles and responsibilities. | Tom Bullington (KBR)
1024 | Construction - Staff Responsibility | Other | Construction - Staff Responsibility | Construction | Quality | Construction - Staff Responsibility | Provide start-up team members the opportunity to review project design documents (P&IDs, electrical single lines and system descriptions). | Tom Bullington (KBR)
1025 | Construction - Staff Responsibility | Other | Construction - Staff Responsibility | Construction | Quality | Construction - Staff Responsibility | Schedule meetings on a regular basis between Construction and start-up team members. | Tom Bullington (KBR)
1026 | Construction - Staff Responsibility | Other | Construction - Staff Responsibility | Construction | Quality | Construction - Staff Responsibility | Develop and integrate the start-up schedule with the overall project schedule in order to provide a clear indication of start-up tasks and time required to perform them. | Tom Bullington (KBR)
1027 | Construction - Staff Responsibility | Other | Construction - Staff Responsibility | Construction | Quality | Construction - Staff Responsibility | Maintain sets of as-built drawings during construction and start-up. | Tom Bullington (KBR)
1028 | Construction - Staff Responsibility | Other | Construction - Staff Responsibility | Construction | Quality | Construction - Staff Responsibility | Ensure that the start-up team is aware of project goals, a definitive start-up plan is developed and management has "bought into" the commissioning/start-up concept. | Tom Bullington (KBR)
1029 | Construction - Staff Responsibility | Other | Construction - Staff Responsibility | Construction | Quality | Construction - Staff Responsibility | Update all E&I required drawings at end of project to reflect "as-built" conditions. | Tom Bullington (KBR)
1030 | Construction - Staff Responsibility | Other | Construction - Staff Responsibility | Construction | Quality | Construction - Staff Responsibility | Provide adequate number of PCs in the field to track material. | Tom Bullington (KBR)
1031 | Construction - Staff Responsibility | Other | Construction - Staff Responsibility | Construction | Quality | Construction - Staff Responsibility | Allocate time and budget for vendor-supplied equipment document reviews and shop testing and inspections to detect design deficiencies prior to fabrication and shipment. | Tom Bullington (KBR)
1032 | Construction - Staff Responsibility | Other | Construction - Staff Responsibility | Construction | Quality | Construction - Staff Responsibility | Establish site program/procedures that assure all equipment received is examined for specification compliance, possible shipping damage, and then properly maintained until installation and start-up. | Tom Bullington (KBR)
1033 | Construction - Staff Responsibility | Other | Construction - Staff Responsibility | Construction | Quality | Construction - Staff Responsibility | Establish a site lubrication program based on manufacturer's specifications for all equipment. | Tom Bullington (KBR)
1034 | Construction - Staff Responsibility | Other | Construction - Staff Responsibility | Construction | Quality | Construction - Staff Responsibility | Note: Most rotating equipment should be "turned" on a regular basis during the construction period to prevent bearing damage. | Tom Bullington (KBR)
1035 | Construction - Staff Responsibility | Other | Construction - Staff Responsibility | Construction | Quality | Construction - Staff Responsibility | Plan on using Wal-Honde pipe alignment tools on thin wall stainless steel piping. | Tom Bullington (KBR)
1036 | Construction - Temporary Facilities | Other | Construction - Temporary Facilities | Construction | Quality | Construction - Temporary Facilities | Outfit the site fabrication shop. Proper and adequate tools and equipment. | Tom Bullington (KBR)
1037 | Construction - Temporary Facilities | Other | Construction - Temporary Facilities | Construction | Quality | Construction - Temporary Facilities | Utilize manufactured items in lieu of field-fabricated items such as: Toilet trailers, Shelving systems, Knockdown temporary buildings, Power distribution panels, Print shacks and gang boxes | Tom Bullington (KBR)
1038 | Construction - Temporary Facilities | Other | Construction - Temporary Facilities | Construction | Quality | Construction - Temporary Facilities | Use CONEX “sea vans or sea trains” with preinstalled shelving, benches, lights and HVAC for satellite tool rooms, mini warehouses and change rooms. | Tom Bullington (KBR)
1039 | Construction - Temporary Facilities | Other | Construction - Temporary Facilities | Construction | Quality | Construction - Temporary Facilities | Provide covered storage with controlled atmosphere for sensitive electrical and instrumentation items. | Tom Bullington (KBR)
1040 | Construction - Temporary Facilities | Other | Construction - Temporary Facilities | Construction | Quality | Construction - Temporary Facilities | Provide adequate bins and shelving for the storage of items such as fittings and small valves. | Tom Bullington (KBR)
1041 | Construction - Temporary Facilities | Other | Construction - Temporary Facilities | Construction | Quality | Construction - Temporary Facilities | Provide racks for storing small pipe, conduit and miscellaneous steel shapes. | Tom Bullington (KBR)
1042 | Construction - Temporary Facilities | Other | Construction - Temporary Facilities | Construction | Quality | Construction - Temporary Facilities | Provide a suitable working surface such as gravel, adequate drainage and sufficient dunnage for laydown areas. | Tom Bullington (KBR)
1043 | Construction - Temporary Facilities | Other | Construction - Temporary Facilities | Construction | Quality | Construction - Temporary Facilities | Provide fabrication shop with adequate safe power and outfit shop with proper and sufficient tools and equipment. | Tom Bullington (KBR)
1044 | Construction - Temporary Facilities | Other | Construction - Temporary Facilities | Construction | Quality | Construction - Temporary Facilities | Layout fabrication shop with the entire fabrication process in mind to maximize efficiency. | Tom Bullington (KBR)
1045 | Construction - Temporary Facilities | Other | Construction - Temporary Facilities | Construction | Quality | Construction - Temporary Facilities | Prepackage satellite fabrication shops in two "Conex" containers complete with tools/equipment, prefabricated roof trusses and roofing material. Set on concrete work slab. | Tom Bullington (KBR)
1046 | Construction - Temporary Facilities | Other | Construction - Temporary Facilities | Construction | Quality | Construction - Temporary Facilities | Utilize single in-plant contractor to maintain construction roads. | Tom Bullington (KBR)
1047 | Construction - Temporary Facilities | Other | Construction - Temporary Facilities | Construction | Quality | Construction - Temporary Facilities | Use interlocking "Unimats" or similar system to "stabilize" and/or protect heavy lift haul roads. | Tom Bullington (KBR)
1048 | Construction - Temporary Facilities | Other | Construction - Temporary Facilities | Construction | Quality | Construction - Temporary Facilities | Install temporary power during installation of underground utilities to reduce exposure to construction equipment. Also, route temporary power along routes least likely to be excavated during construction. | Tom Bullington (KBR)
1049 | Construction - Temporary Facilities | Other | Construction - Temporary Facilities | Construction | Quality | Construction - Temporary Facilities | Ensure that sufficient temporary power is available for checkout and start-up or that permanent power will be available to support these activities. | Tom Bullington (KBR)
1050 | Construction - Temporary Facilities | Other | Construction - Temporary Facilities | Construction | Quality | Construction - Temporary Facilities | Install electric drinking fountains early to eliminate the need for water cans. Locate fountains or bottled water fountains near electrical distribution panels. | Tom Bullington (KBR)
1051 | Construction - Temporary Facilities | Other | Construction - Temporary Facilities | Construction | Quality | Construction - Temporary Facilities | Maximize the use of permanent piping systems for temporary services (air, N2, and water). | Tom Bullington (KBR)
1052 | Construction - Temporary Facilities | Other | Construction - Temporary Facilities | Construction | Quality | Construction - Temporary Facilities | Utilize bar coded swipe cards or similar electronic time keeping system. | Tom Bullington (KBR)
1053 | Construction - Temporary Facilities | Other | Construction - Temporary Facilities | Construction | Quality | Construction - Temporary Facilities | Consider the use of electronic security systems. | Tom Bullington (KBR)
1054 | Construction - Temporary Facilities | Other | Construction - Temporary Facilities | Construction | Quality | Construction - Temporary Facilities | Consider the following when selecting the security contractor and setting up the security program for the project. (Ability to contact 911, Controlled access at construction gates, Security/safety of in-plant roads and parking, and Roving patrol for on-site facilities | Tom Bullington (KBR)
1055 | Construction - Temporary Facilities | Other | Construction - Temporary Facilities | Construction | Quality | Construction - Temporary Facilities | Utilize prefabricated trailers (double wide trailers, multiple single wide, etc.) for Construction "Site" Offices. | Tom Bullington (KBR)
1056 | Construction - Temporary Facilities | Other | Construction - Temporary Facilities | Construction | Quality | Construction - Temporary Facilities | Are temporary facilities supplied by subcontractor and owner clearly defined? | Tom Bullington (KBR)
1057 | Construction - Temporary Facilities | Other | Construction - Temporary Facilities | Construction | Quality | Construction - Temporary Facilities | Design sanitary sewer system early to minimize use of chemical toilets. | Tom Bullington (KBR)
1058 | Construction - Temporary Facilities | Other | Construction - Temporary Facilities | Construction | Quality | Construction - Temporary Facilities | Develop a network computer system and provide for fax, E-Mail and copying systems. | Tom Bullington (KBR)
1059 | Construction - Temporary Facilities | Other | Construction - Temporary Facilities | Construction | Quality | Construction - Temporary Facilities | Investigate alternatives to minimize problems due to limited on-site parking - such as busing from outlying communities or shuttle buses from remote parking lots | Tom Bullington (KBR)
1060 | Construction - Temporary Facilities | Other | Construction - Temporary Facilities | Construction | Quality | Construction - Temporary Facilities | Look at alternate parking schemes such as parking vehicles end-to-end when laying out parking lots. | Tom Bullington (KBR)
1061 | Construction - Temporary Facilities | Other | Construction - Temporary Facilities | Construction | Quality | Construction - Temporary Facilities | Assess temporary power requirements jointly between Engineering, Construction and [Client] to ensure a safe, cost effective and usable system, taking the following into consideration: Develop one-line Elementaries, routing on plot plan with service requirements, above ground distribution system requirements | Tom Bullington (KBR)
1062 | Construction - Temporary Facilities | Other | Construction - Temporary Facilities | Construction | Quality | Construction - Temporary Facilities | Use of new or existing permanent plant facilities for temporary facilities during construction. | Tom Bullington (KBR)
1063 | Construction - Temporary Facilities | Other | Construction - Temporary Facilities | Construction | Quality | Construction - Temporary Facilities | Establish requirements for Subcontractors Office Trailer Area | Tom Bullington (KBR)
1064 | Construction - Temporary Facilities | Other | Construction - Temporary Facilities | Construction | Quality | Construction - Temporary Facilities | Establish requirements for Warehouses | Tom Bullington (KBR)
1065 | Construction - Temporary Facilities | Other | Construction - Temporary Facilities | Construction | Quality | Construction - Temporary Facilities | Establish requirements for Laydown Areas | Tom Bullington (KBR)
1066 | Construction - Temporary Facilities | Other | Construction - Temporary Facilities | Construction | Quality | Construction - Temporary Facilities | Establish requirements for Parking | Tom Bullington (KBR)
1067 | Construction - Temporary Facilities | Other | Construction - Temporary Facilities | Construction | Quality | Construction - Temporary Facilities | Establish requirements for Fabrication and Metal Shops | Tom Bullington (KBR)
1068 | Construction - Temporary Facilities | Other | Construction - Temporary Facilities | Construction | Quality | Construction - Temporary Facilities | Establish requirements for Medical Facility | Tom Bullington (KBR)
1069 | Construction - Temporary Facilities | Other | Construction - Temporary Facilities | Construction | Quality | Construction - Temporary Facilities | Establish requirements for Safety Facility | Tom Bullington (KBR)
1070 | Construction - Temporary Facilities | Other | Construction - Temporary Facilities | Construction | Quality | Construction - Temporary Facilities | Establish requirements for Welder Testing | Tom Bullington (KBR)
1071 | Construction - Temporary Facilities | Other | Construction - Temporary Facilities | Construction | Quality | Construction - Temporary Facilities | Establish requirements for Rigging Testing | Tom Bullington (KBR)
1072 | Construction - Temporary Facilities | Other | Construction - Temporary Facilities | Construction | Quality | Construction - Temporary Facilities | Establish requirements for On Site testing labs (soils, concrete, NDE) | Tom Bullington (KBR)
1073 | Construction - Temporary Facilities | Other | Construction - Temporary Facilities | Construction | Quality | Construction - Temporary Facilities | Establish requirements for Carpenter Shop | Tom Bullington (KBR)
1074 | Construction - Temporary Facilities | Other | Construction - Temporary Facilities | Construction | Quality | Construction - Temporary Facilities | Establish requirements for Portable Toilets | Tom Bullington (KBR)
1075 | Construction - Temporary Facilities | Other | Construction - Temporary Facilities | Construction | Quality | Construction - Temporary Facilities | Establish requirements for Resource Camps | Tom Bullington (KBR)
1076 | Construction - Temporary Facilities | Other | Construction - Temporary Facilities | Construction | Quality | Construction - Temporary Facilities | Establish requirements for Lunch Tents | Tom Bullington (KBR)
1077 | Construction - Temporary Facilities | Other | Construction - Temporary Facilities | Construction | Quality | Construction - Temporary Facilities | Establish requirements for Lunch Tents | Tom Bullington (KBR)
1078 | Construction - Temporary Facilities | Other | Construction - Temporary Facilities | Construction | Quality | Construction - Temporary Facilities | Determine whether any of the permanent facilities can be made available during construction. If so and if a new facility, complete design early on the facility that is to be used during construction. | Tom Bullington (KBR)
1079 | Construction - Temporary Facilities | Other | Construction - Temporary Facilities | Construction | Quality | Construction - Temporary Facilities | Determine whether any of the permanent facilities can be made available during construction. If so and if a new facility, complete design early on the facility that is to be used during construction. | Tom Bullington (KBR)
1080 | Construction - Temporary Facilities | Other | Construction - Temporary Facilities | Construction | Quality | Construction - Temporary Facilities | Give consideration for systems and services that can be used during construction and transferred later on to maintenance or operations. Examples are: personal computers, spare parts software, bar code readers, 2 way radios, cell phones, pagers, portable power tools and shop equipment, pre-engineered builders and packaged air compressors | Tom Bullington (KBR)
1081 | Construction - Temporary Facilities | Other | Construction - Temporary Facilities | Construction | Quality | Construction - Temporary Facilities | If possible, utilize the permanent fencing for job site and/or laydown area security during construction. | Tom Bullington (KBR)
1082 | Construction - Temporary Facilities | Other | Construction - Temporary Facilities | Construction | Quality | Construction - Temporary Facilities | Preplan laydown area layout so that stored items are easy to find, maintain (if required) and remove. | Tom Bullington (KBR)
1083 | Construction - Temporary Facilities | Other | Construction - Temporary Facilities | Construction | Quality | Construction - Temporary Facilities | Consider using pre-engineered metal structures or modular prefabricated construction for buildings and warehouse. | Tom Bullington (KBR)
1084 | Construction - Testing | Other | Construction - Testing | Construction | Quality | Construction - Testing | Expedite hydro testing. Utilize directional ultra sonic detector to quickly pinpoint leaks. | Tom Bullington (KBR)
1085 | Construction - Testing | Other | Construction - Testing | Construction | Quality | Construction - Testing | Provide clean, dry air for the checkout of pneumatic controls. Utilize permanent system or use air receiver/filter dryer to remove moisture from the air. | Tom Bullington (KBR)
1086 | Construction - Testing | Other | Construction - Testing | Construction | Quality | Construction - Testing | Discuss performance test procedures and methods with [Client] as early as possible in order to identify what will be accomplished during the testing. | Tom Bullington (KBR)
1087 | Construction - Testing | Other | Construction - Testing | Construction | Quality | Construction - Testing | Review project Contract for commissioning, start-up and performance test requirements. | Tom Bullington (KBR)
1088 | Construction - Testing | Other | Construction - Testing | Construction | Quality | Construction - Testing | Develop definitive performance test procedures and ensure they are followed. | Tom Bullington (KBR)
1089 | Construction - Testing | Other | Construction - Testing | Construction | Quality | Construction - Testing | Develop an overall test plan in order to coordinate all phases of the facility testing. | Tom Bullington (KBR)
1090 | Construction - Testing | Other | Construction - Testing | Construction | Quality | Construction - Testing | Establish guidelines for determining when the plant is ready for testing. | Tom Bullington (KBR)
1091 | Construction - Testing | Other | Construction - Testing | Construction | Quality | Construction - Testing | Consider means of simplifying and controlling flushing operation in coordination with Plant operations. | Tom Bullington (KBR)
1092 | Construction - Testing | Other | Construction - Testing | Construction | Quality | Construction - Testing | Test plumbing before constructing masonry walls. | Tom Bullington (KBR)
1093 | Construction - Testing | Other | Construction - Testing | Construction | Quality | Construction - Testing | After start-up, all slide-gate valve bolts should be re-tightened. | Tom Bullington (KBR)
1094 | Construction - Testing | Other | Construction - Testing | Construction | Quality | Construction - Testing | Establish lockout/tag out procedures to be uniformly used throughout construction, startup and operations. | Tom Bullington (KBR)
1095 | Construction - Testing | Other | Construction - Testing | Construction | Quality | Construction - Testing | Form a pre-commissioning team with Owner, Contractors) and Subcontractors). | Tom Bullington (KBR)
1096 | Construction - Tools | Other | Construction - Tools | Construction | Quality | Construction - Tools | Minimize pipe and tubing weld and preparation labor. Utilize hand-held air-operated high speed milling tools. | Tom Bullington (KBR)
1097 | Construction - Tools | Other | Construction - Tools | Construction | Quality | Construction - Tools | Maximize thin wall tubing installation productivity. For highly repetitive joints, consider using autogenous orbital welding equipment. | Tom Bullington (KBR)
1098 | Construction - Tools | Other | Construction - Tools | Construction | Quality | Construction - Tools | Maximize metal cutting productivity. Use lightweight portable add-on plasma cutting machine in lieu of oxy-acetylene cutting ("Pow Con Starcut"). | Tom Bullington (KBR)
1099 | Construction - Tools | Other | Construction - Tools | Construction | Quality | Construction - Tools | Investigate feasibility of using pen-based computers for take-offs and punch lists. Plan for set-up and training time @ site. | Tom Bullington (KBR)
1100 | Construction - Tools | Other | Construction - Tools | Construction | Quality | Construction - Tools | Use bar coded identification system to aid in tool and bulk material inventory control. | Tom Bullington (KBR)
1101 | Construction - Tools | Other | Construction - Tools | Construction | Quality | Construction - Tools | Keep a sufficient supply of consumable supplies such as saw blades, files, and welding rod on hand in fabrication shops). | Tom Bullington (KBR)
1102 | Construction - Tools | Other | Construction - Tools | Construction | Quality | Construction - Tools | Provide centrally located "engineered" oxygen/acetylene bottle storage racks. Consider using bulk gas supply with a permanent distribution system. | Tom Bullington (KBR)
1103 | Construction - Tools | Other | Construction - Tools | Construction | Quality | Construction - Tools | Since the availability of open radio channels may be limited, investigate alternative means of communications such as pagers and cellular phones. | Tom Bullington (KBR)
1104 | Construction - Tools | Other | Construction - Tools | Construction | Quality | Construction - Tools | Order small tools and extension cords with twist lock plugs for temporary power usage. | Tom Bullington (KBR)
1105 | Construction - Tools | Other | Construction - Tools | Construction | Quality | Construction - Tools | Ensure that power tools have lock-on button removed before arrival at job site. Specify this requirement in small tool orders to eliminate need for removal of buttons at job site. | Tom Bullington (KBR)
1106 | Construction - Tools | Other | Construction - Tools | Construction | Quality | Construction - Tools | Utilize prefabricated temporary construction power units. | Tom Bullington (KBR)
1107 | Construction - Tools | Other | Construction - Tools | Construction | Quality | Construction - Tools | Specify use of laser type survey equipment for elevation and centerlines. | Tom Bullington (KBR)
1108 | Construction - Turnover | Other | Construction - Turnover | Startup | Quality | Construction - Turnover | Ensure that a single punch list is used by construction and startup to track system completion requirements. | Tom Bullington (KBR)
1109 | Construction - Turnover | Other | Construction - Turnover | Startup | Quality | Construction - Turnover | Establish requirements to be met for early turnovers to [Client]. | Tom Bullington (KBR)
1110 | Construction - Turnover | Other | Construction - Turnover | Startup | Quality | Construction - Turnover | Need early and precise definition of system packages for phased ordered completion turnover. | Tom Bullington (KBR)
1111 | Construction - Turnover | Other | Construction - Turnover | Startup | Quality | Construction - Turnover | Develop a proper Turnover program, complete with punch listing and system statusing program. | Tom Bullington (KBR)
1112 | Construction - Turnover | Other | Construction - Turnover | Startup | Quality | Construction - Turnover | Define and prepare system turnover packages well in advance to allow for prioritizing construction activities. | Tom Bullington (KBR)
1113 | Construction - Turnover | Other | Construction - Turnover | Startup | Quality | Construction - Turnover | Start punch-out of facilities at earliest date possible and involve the project Process engineers. Do not underestimate the time required to complete punch list work. | Tom Bullington (KBR)
1114 | Construction - Turnover | Other | Construction - Turnover | Startup | Quality | Construction - Turnover | Ensure all required documentation is completed as required and on schedule. | Tom Bullington (KBR)
1115 | Construction - Turnover | Other | Construction - Turnover | Startup | Quality | Construction - Turnover | Involve plant personnel in commissioning and start-up planning. (Early) | Tom Bullington (KBR)
1116 | Control Systems - Cable | I&C | Control Systems - Cable | Design | Quality | Control Systems - Cable | Specify multi-pair cable, where possible. | Tom Bullington (KBR)
1117 | Control Systems - Cable | I&C | Control Systems - Cable | Design | Quality | Control Systems - Cable | Review use of armored cable and tray for above ground instruments in lieu of conduit. | Tom Bullington (KBR)
1118 | Control Systems - Cable | I&C | Control Systems - Cable | Design | Quality | Control Systems - Cable | Provide Quality tracking of instrument cable from specification to installation. | Tom Bullington (KBR)
1119 | Control Systems - Conduit | Electrical | Control Systems - Conduit | Design | Quality | Control Systems - Conduit | Clearly define on detail drawings where conduit seal fittings are required. | Tom Bullington (KBR)
1120 | Control Systems - Conduit | Electrical | Control Systems - Conduit | Design | Quality | Control Systems - Conduit | Purchase 1/2" flex conduit for instrument conduit connections (3/4" hard to work). | Tom Bullington (KBR)
1121 | Control Systems - Conduit | Electrical | Control Systems - Conduit | Design | Quality | Control Systems - Conduit | Use LBD fitting to enter side of instrument junction boxes for home run cables (T fitting violates bending radius of cable). (REVIEW) | Tom Bullington (KBR)
1122 | Control Systems - Conduit | Electrical | Control Systems - Conduit | Design | Quality | Control Systems - Conduit | Install flex coupling in locations where vibration frequencies occur. | Tom Bullington (KBR)
1123 | Control Systems - Conduit | Electrical | Control Systems - Conduit | Design | Quality | Control Systems - Conduit | Show instrument conduit on drawings (point to point). | Tom Bullington (KBR)
1124 | Control Systems - Conduit | Electrical | Control Systems - Conduit | Design | Quality | Control Systems - Conduit | Do not install ground wire on instrument flex conduit unless [Client] requests. Flex conduit has built in ground up to 1-1/4". | Tom Bullington (KBR)
1125 | Control Systems - Control Building | I&C | Control Systems - Control Building | Design | Quality | Control Systems - Control Building | Ensure that door openings are designed to accommodate installation of DCS and that any required special lifting devices for top heavy equipment are included in the purchase order. | Tom Bullington (KBR)
1126 | Control Systems - Control Building | I&C | Control Systems - Control Building | Design | Quality | Control Systems - Control Building | Analyzer Sample Shelters combined when applicable to one vendor / shelter. Combine continuous emission monitoring system and water / steam sample into a common shelter. | Tom Bullington (KBR)
1127 | Control Systems - Design Considerations | I&C | Control Systems - Design Considerations | Design | Quality | Control Systems - Design Considerations | Select DCS supplier early. | Tom Bullington (KBR)
1128 | Control Systems - Design Considerations | I&C | Control Systems - Design Considerations | Design | Quality | Control Systems - Design Considerations | Establish "teamwork" plan between Engineering, [Client] and DCS supplier. | Tom Bullington (KBR)
1129 | Control Systems - Design Considerations | I&C | Control Systems - Design Considerations | Design | Quality | Control Systems - Design Considerations | As process information and in-line instrument information become available, procure in-line devices to support piping schedule. | Tom Bullington (KBR)
1130 | Control Systems - Design Considerations | I&C | Control Systems - Design Considerations | Design | Quality | Control Systems - Design Considerations | Ensure that piping and instrument items related to vessel trim are specified on drawings and included on initial bulk purchases. | Tom Bullington (KBR)
1131 | Control Systems - Design Considerations | I&C | Control Systems - Design Considerations | Design | Quality | Control Systems - Design Considerations | Review position and configuration of instrument bridles on vessels and piping for access and to prevent OBSTRUCTING walkways and platforms. | Tom Bullington (KBR)
1132 | Control Systems - Design Considerations | I&C | Control Systems - Design Considerations | Design | Quality | Control Systems - Design Considerations | Perform thorough review of supplier drawings with regards to controls and instruments (i.e., valve motor controls and general circuitry). | Tom Bullington (KBR)
1133 | Control Systems - Design Considerations | I&C | Control Systems - Design Considerations | Design | Quality | Control Systems - Design Considerations | Pre-assemble instrument manifolds and prefabricate instrument stands, when practical. | Tom Bullington (KBR)
1134 | Control Systems - Design Considerations | I&C | Control Systems - Design Considerations | Design | Quality | Control Systems - Design Considerations | Engineer is to make certain that a vendor / supplier’s connection drawings are crosschecked with AFC drawings to ensure the contacts to be used when terminating at an individual instrument or device are consistent. | Tom Bullington (KBR)
1135 | Control Systems - Design Considerations | I&C | Control Systems - Design Considerations | Design | Quality | Control Systems - Design Considerations | Engineer to use the Master Equipment List numbering / tagging system on all critical E&I components. Issue a complete E&I index listing all tagged control items. | Tom Bullington (KBR)
1136 | Control Systems - Design Considerations | I&C | Control Systems - Design Considerations | Design | Quality | Control Systems - Design Considerations | Issue wire tags from home office (package by drawing). (Utilize database to allow this) | Tom Bullington (KBR)
1137 | Control Systems - Design Considerations | I&C | Control Systems - Design Considerations | Design | Quality | Control Systems - Design Considerations | Demo drawings should indicate instruments that will be reused to be removed before pipe is demoed. | Tom Bullington (KBR)
1138 | Control Systems - Instruments | I&C | Control Systems - Instruments | Design | Quality | Control Systems - Instruments | Procure instruments of proven quality. When assembling bid list for instrument suppliers, make known any verifiable problems or negative experiences with a supplier. | Tom Bullington (KBR)
1139 | Control Systems - Instruments | I&C | Control Systems - Instruments | Design | Quality | Control Systems - Instruments | Carefully check length of thermocouples prior to ordering. (Engineering review of POs). | Tom Bullington (KBR)
1140 | Control Systems - Instruments | I&C | Control Systems - Instruments | Design | Quality | Control Systems - Instruments | Require that all engineered instruments be tagged with stainless steel tag by the supplier. | Tom Bullington (KBR)
1141 | Control Systems - Instruments | I&C | Control Systems - Instruments | Design | Quality | Control Systems - Instruments | Specify thermal enclosures for freeze protection of instruments that are mounted outside. | Tom Bullington (KBR)
1142 | Control Systems - Instruments | I&C | Control Systems - Instruments | Design | Quality | Control Systems - Instruments | When practical, specify that instruments be “shop” calibrated prior to being shipped to the field. Critical long lead instruments need to be identified for this exercise if pre-calibration is not performed in the field. | Tom Bullington (KBR)
1143 | Control Systems - Instruments | I&C | Control Systems - Instruments | Design | Quality | Control Systems - Instruments | Specify standardized instrument fittings for the project, including vendors. | Tom Bullington (KBR)
1144 | Control Systems - Instruments | I&C | Control Systems - Instruments | Design | Quality | Control Systems - Instruments | Maximize use of line-mounted instruments as opposed to stand mounts when possible. | Tom Bullington (KBR)
1145 | Control Systems - Junction Boxes | I&C | Control Systems - Junction Boxes | Design | Quality | Control Systems - Junction Boxes | Utilize prefabricated instrument panels. | Tom Bullington (KBR)
1146 | Control Systems - Junction Boxes | I&C | Control Systems - Junction Boxes | Design | Quality | Control Systems - Junction Boxes | Have vendor tag terminals in instrument Junction boxes as indicated on drawings. | Tom Bullington (KBR)
1147 | Control Systems - Loop Drawings | I&C | Control Systems - Loop Drawings | Design | Quality | Control Systems - Loop Drawings | Ensure loop drawings include instrument set points, etc. | Tom Bullington (KBR)
1148 | Control Systems - Loop Drawings | I&C | Control Systems - Loop Drawings | Design | Quality | Control Systems - Loop Drawings | Ensure loop drawings encompass workstation to field device. | Tom Bullington (KBR)
1149 | Control Systems - Testing | I&C | Control Systems - Testing | Design | Quality | Control Systems - Testing | Consider the following concerning loop checking, calibration and testing of instruments: Issue loop diagrams promptly, Develop installation plan so that calibration can be planned and completed in an orderly manner and Set up turnover sequence, develop loop-checking plan, and identify required work force needs | Tom Bullington (KBR)
1150 | Control Systems - Testing | I&C | Control Systems - Testing | Design | Quality | Control Systems - Testing | Involve key plant maintenance and operations personnel in planning E&I checkout and start-up processes. | Tom Bullington (KBR)
1151 | Control Systems - Testing | I&C | Control Systems - Testing | Design | Quality | Control Systems - Testing | Recalibrate instruments as received at site. Instrument calibration information should be sent to the field early on. Coordinate with Instrument Support. | Tom Bullington (KBR)
1152 | Control Systems - Tubing | I&C | Control Systems - Tubing | Design | Quality | Control Systems - Tubing | Pre-insulated tubing is preferable to hand insulated piping for steam tracing supply and return lines as well as for instrumentation sensing leads. | Tom Bullington (KBR)
1153 | Control Systems - Tubing | I&C | Control Systems - Tubing | Design | Quality | Control Systems - Tubing | Make maximum use of multi-tube bundles. | Tom Bullington (KBR)
1154 | Control Systems - Tubing | I&C | Control Systems - Tubing | Design | Quality | Control Systems - Tubing | Standardize tubing grades and wall thickness for stainless steel tubing. | Tom Bullington (KBR)
1155 | Control Systems - Tubing | I&C | Control Systems - Tubing | Design | Quality | Control Systems - Tubing | Standardize tubing valves, including vendor valves. | Tom Bullington (KBR)
1156 | Control Systems - Vendor Requirements | I&C | Control Systems - Vendor Requirements | Design | Quality | Control Systems - Vendor Requirements | Require that supplier furnished "packaged units" provide job standard instrumentation hardware, identification tag numbers, and specification sheets in order to properly check and calibrate these instruments in the field. Supplier furnished items shipped in crates separate from machines (i.e., compressor and turbine) should also identify items by "Bill of Material" and purchase order number. | Tom Bullington (KBR)
1157 | Control Systems - Vendor Requirements | I&C | Control Systems - Vendor Requirements | Design | Quality | Control Systems - Vendor Requirements | Engineering must specify any special preventive maintenance and storage requirements for instrument hardware. Provide list and have supplier post signs on shipping crates. | Tom Bullington (KBR)
1158 | Control Systems - Vendor Requirements | I&C | Control Systems - Vendor Requirements | Design | Quality | Control Systems - Vendor Requirements | DCS equipment should be set up for delivery to the job site after special environmental storage conditions (HVAC) are available. | Tom Bullington (KBR)
1159 | Control Systems - Vendor Requirements | I&C | Control Systems - Vendor Requirements | Design | Quality | Control Systems - Vendor Requirements | Include supplier representative's hourly rate clauses in POs for DCS and other specialized equipment. | Tom Bullington (KBR)
1160 | Control Systems - Vendor Requirements | I&C | Control Systems - Vendor Requirements | Design | Quality | Control Systems - Vendor Requirements | Consider in-house supplier representative for DCS system when configuring and developing DCS software for large projects. | Tom Bullington (KBR)
1161 | Control Systems - Vendor Requirements | I&C | Control Systems - Vendor Requirements | Design | Quality | Control Systems - Vendor Requirements | Issue the instrument index as early as possible (after AFC P&IDs) so it can be used in identifying, controlling, and referencing instruments. | Tom Bullington (KBR)
1162 | Electrical - Automation | Electrical | Electrical - Automation | Design | Quality | Electrical - Automation | Review feasibility of PDS modeling all conduit and raceways of 3” and larger site wide for interference checking. | Tom Bullington (KBR)
1163 | Electrical - Automation | Electrical | Electrical - Automation | Design | Quality | Electrical - Automation | Identify on PDS modeling hazardous area boundaries on above ground electrical power conduit drawings. Refer to actual hazardous location plans | Tom Bullington (KBR)
1164 | Electrical - Cable Power | Electrical | Electrical - Cable Power | Design | Quality | Electrical - Cable Power | For 20 feet pipe rack bays, use non-standard 20' sections of cable tray (same cost, longer delivery). | Tom Bullington (KBR)
1165 | Electrical - Cable Power | Electrical | Electrical - Cable Power | Design | Quality | Electrical - Cable Power | Minimize cable trays running under welded piping. | Tom Bullington (KBR)
1166 | Electrical - Cable Power | Electrical | Electrical - Cable Power | Design | Quality | Electrical - Cable Power | Group elevated cable junctions in as few places as possible to minimize scaffolding needs. | Tom Bullington (KBR)
1167 | Electrical - Cable Power | Electrical | Electrical - Cable Power | Design | Quality | Electrical - Cable Power | Assure that cable tray barriers when required are purchased for tray fittings also. | Tom Bullington (KBR)
1168 | Electrical - Cable Power | Electrical | Electrical - Cable Power | Design | Quality | Electrical - Cable Power | Minimize the use of cable tray fitting when possible; do not reduce tray size for short distance when possible. Cable tray reduction positioned at structural steel to minimize need for additional tray support steel | Tom Bullington (KBR)
1169 | Electrical - Cable Power | Electrical | Electrical - Cable Power | Design | Quality | Electrical - Cable Power | Squad checks tray drop out support steel to assure correct location and design will allow tray to anchor to steel without adding angle iron. | Tom Bullington (KBR)
1170 | Electrical - Cable Tray | Electrical | Electrical - Cable Tray | Design | Quality | Electrical - Cable Tray | Cable tray drawings should be issued along with miscellaneous structural steel supports required for installation. | Tom Bullington (KBR)
1171 | Electrical - Cable Tray | Electrical | Electrical - Cable Tray | Design | Quality | Electrical - Cable Tray | Review use of Hilti studs to install tray directly to structural steel | Tom Bullington (KBR)
1172 | Electrical - Cable Tray | Electrical | Electrical - Cable Tray | Design | Quality | Electrical - Cable Tray | If cable trays are stacked, there should be a minimum of 18 inches to facilitate pulling cable and installing tray covers. | Tom Bullington (KBR)
1173 | Electrical - Conduit | Electrical | Electrical - Conduit | Design | Quality | Electrical - Conduit | The use of PVC Conduit for underground installation should be used when possible. | Tom Bullington (KBR)
1174 | Electrical - Conduit | Electrical | Electrical - Conduit | Design | Quality | Electrical - Conduit | Conduit stub-ups under raised floors or in termination rooms should be located near doors when possible to make wire pulling less costly; avoid stub-ups directly under equipment if possible. | Tom Bullington (KBR)
1175 | Electrical - Conduit | Electrical | Electrical - Conduit | Design | Quality | Electrical - Conduit | Review duct bank and manhole layouts to keep bends to a minimum. | Tom Bullington (KBR)
1176 | Electrical - Conduit | Electrical | Electrical - Conduit | Design | Quality | Electrical - Conduit | Call out need for oversized fittings (if required) when sleeving cables (to meet bending radius requirements). | Tom Bullington (KBR)
1177 | Electrical - Conduit | Electrical | Electrical - Conduit | Design | Quality | Electrical - Conduit | Show conduit routing on drawings (point to point). Indicate location of seals required for area class changes and location of expansion joints. | Tom Bullington (KBR)
1178 | Electrical - Conduit | Electrical | Electrical - Conduit | Design | Quality | Electrical - Conduit | Route conduit and small piping, instrument leads, behind stairwells for easy installation without using expensive temporary scaffolding or personnel baskets. Very often such conduit and small pipe is designed for remote installation on the outside of the structure because "there is no interference," but is costly to install and maintain, and increases fall exposures. | Tom Bullington (KBR)
1179 | Electrical - Conduit | Electrical | Electrical - Conduit | Design | Quality | Electrical - Conduit | Conduit connections to equipment should be flexible as opposed to rigid. Rigid conduit is difficult to align prior to equipment installation. | Tom Bullington (KBR)
1180 | Electrical - Conduit | Electrical | Electrical - Conduit | Design | Quality | Electrical - Conduit | Conduit stub outs for building need to extend at least 5 feet beyond the building foundation | Tom Bullington (KBR)
1181 | Electrical - Conduit | Electrical | Electrical - Conduit | Design | Quality | Electrical - Conduit | Indicate location of platform utility station locations to assure conduit and steam line awareness. | Tom Bullington (KBR)
1182 | Electrical - Conduit | Electrical | Electrical - Conduit | Design | Quality | Electrical - Conduit | Assure that field is made aware of equipment that expands (and how much) to establish clear conduit routing locations and expansion joint locations requirements. | Tom Bullington (KBR)
1183 | Electrical - Conduit | Electrical | Electrical - Conduit | Design | Quality | Electrical - Conduit | Minimize the depth of duct banks at all times where possible. | Tom Bullington (KBR)
1184 | Electrical - Conduit | Electrical | Electrical - Conduit | Design | Quality | Electrical - Conduit | Maximize the use of conduit bends rather than fitting where possible on A.G. conduit runs. | Tom Bullington (KBR)
1185 | Electrical - Design Considerations | Electrical | Electrical - Design Considerations | Design | Quality | Electrical - Design Considerations | Electrical drawings should reference Civil drawings that detail appurtenances (supports, block outs, embeds, etc.) to accommodate electrical conduit. | Tom Bullington (KBR)
1186 | Electrical - Design Considerations | Electrical | Electrical - Design Considerations | Design | Quality | Electrical - Design Considerations | Review design to eliminate multiple runs of conduit by replacement with an equivalent tray and to improve sequencing. | Tom Bullington (KBR)
1187 | Electrical - Design Considerations | Electrical | Electrical - Design Considerations | Design | Quality | Electrical - Design Considerations | Ensure that design understands that a construction deliverable is a database with which to print wire markers. | Tom Bullington (KBR)
1188 | Electrical - Design Considerations | Electrical | Electrical - Design Considerations | Design | Quality | Electrical - Design Considerations | Use an equipment tagging system on all electrical equipment. | Tom Bullington (KBR)
1189 | Electrical - Design Considerations | Electrical | Electrical - Design Considerations | Design | Quality | Electrical - Design Considerations | Standardize equipment, e.g., MCCs, switchgear and small transformers. | Tom Bullington (KBR)
1190 | Electrical - Design Considerations | Electrical | Electrical - Design Considerations | Design | Quality | Electrical - Design Considerations | Substation modules with switchgear, MCCs, LP panels should be considered. | Tom Bullington (KBR)
1191 | Electrical - Design Considerations | Electrical | Electrical - Design Considerations | Design | Quality | Electrical - Design Considerations | Utilize standard manufactured equipment whenever possible. | Tom Bullington (KBR)
1192 | Electrical - Design Considerations | Electrical | Electrical - Design Considerations | Design | Quality | Electrical - Design Considerations | Determine best location of controls on equipment for safety and easy operation. | Tom Bullington (KBR)
1193 | Electrical - Design Considerations | Electrical | Electrical - Design Considerations | Design | Quality | Electrical - Design Considerations | Locate oil level sight gauges for easy operator access. | Tom Bullington (KBR)
1194 | Electrical - Design Considerations | Electrical | Electrical - Design Considerations | Design | Quality | Electrical - Design Considerations | Assure that all E&I equipment that appears on all single lines and wiring diagrams is properly tagged and numbered according to the specs. | Tom Bullington (KBR)
1195 | Electrical - Design Considerations | Electrical | Electrical - Design Considerations | Design | Quality | Electrical - Design Considerations | Endeavor to obtain early designs for vessel electrics in order to complete electrical work in conjunction with vessel and piping work. | Tom Bullington (KBR)
1196 | Electrical - Design Considerations | Electrical | Electrical - Design Considerations | Design | Quality | Electrical - Design Considerations | Establish any special tools or installation equipment required and ensures they are ordered with the main equipment PO. | Tom Bullington (KBR)
1197 | Electrical - Design Considerations | Electrical | Electrical - Design Considerations | Design | Quality | Electrical - Design Considerations | Incorporate well-defined equipment specifications into one document. | Tom Bullington (KBR)
1198 | Electrical - Design Considerations | Electrical | Electrical - Design Considerations | Design | Quality | Electrical - Design Considerations | Review feasibility of Underground (U/G) vs. Aboveground (A/G) cable routing. | Tom Bullington (KBR)
1199 | Electrical - Design Considerations | Electrical | Electrical - Design Considerations | Design | Quality | Electrical - Design Considerations | Engineering should establish clear corridors on electrical and piping design drawings for deluge system during early design. | Tom Bullington (KBR)
1200 | Electrical - Design Considerations | Electrical | Electrical - Design Considerations | Design | Quality | Electrical - Design Considerations | Portions of work which can be pushed ahead to relieve later peaking of critical crafts should be identified/scheduled. | Tom Bullington (KBR)
1201 | Electrical - Design Considerations | Electrical | Electrical - Design Considerations | Design | Quality | Electrical - Design Considerations | Layout equipment for most efficient operations. | Tom Bullington (KBR)
1202 | Electrical - Design Considerations | Electrical | Electrical - Design Considerations | Design | Quality | Electrical - Design Considerations | Review with plant operations and maintenance where all control/emergency stop stations should be located throughout the production area | Tom Bullington (KBR)
1203 | Electrical - Design Considerations | Electrical | Electrical - Design Considerations | Design | Quality | Electrical - Design Considerations | Ensure that design meets OSHA (and [Client]) requirements for lockable disconnects within sight of equipment. | Tom Bullington (KBR)
1204 | Electrical - Grounding | Electrical | Electrical - Grounding | Design | Quality | Electrical - Grounding | Grounding drawings should be issued before or in conjunction with civil drawings. Allow grounding under slab to be placed in sand bed under slab, rather than buried in a ditch. | Tom Bullington (KBR)
1205 | Electrical - Grounding | Electrical | Electrical - Grounding | Design | Quality | Electrical - Grounding | The use of embedded grounding pads inside substation buildings should be installed to ground equipment when possible. | Tom Bullington (KBR)
1206 | Electrical - Grounding | Electrical | Electrical - Grounding | Design | Quality | Electrical - Grounding | Ground wire between cable and trays and conduits as required by NEC should be shown on drawings. | Tom Bullington (KBR)
1207 | Electrical - Grounding | Electrical | Electrical - Grounding | Design | Quality | Electrical - Grounding | Ensure that grounding clips are installed on fireproofed steel at time of fabrication. | Tom Bullington (KBR)
1208 | Electrical - Grounding | Electrical | Electrical - Grounding | Design | Quality | Electrical - Grounding | Grounding stub up locations need to be verified with vessel and equipment ground clip locations. | Tom Bullington (KBR)
1209 | Electrical - Grounding | Electrical | Electrical - Grounding | Design | Quality | Electrical - Grounding | PVC conduit to support ground wire should be used when possible (eliminates requirement to ground conduit sleeve). | Tom Bullington (KBR)
1210 | Electrical - Grounding | Electrical | Electrical - Grounding | Design | Quality | Electrical - Grounding | Consider the use of fiberglass ground wells rather than the clay pipe. | Tom Bullington (KBR)
1211 | Electrical - Lighting | Electrical | Electrical - Lighting | Design | Quality | Electrical - Lighting | The early issue of lighting plans & details for street, area, & buildings. Lighting will reduce need for the installation of temporary lighting. | Tom Bullington (KBR)
1212 | Electrical - Lighting | Electrical | Electrical - Lighting | Design | Quality | Electrical - Lighting | Color code lighting and CKT wiring Black, red and Blue. Color code neutral white wiring with CKT color tracer. | Tom Bullington (KBR)
1213 | Electrical - Lighting | Electrical | Electrical - Lighting | Design | Quality | Electrical - Lighting | Maximize the use of floodlighting from platforms where possible. | Tom Bullington (KBR)
1214 | Electrical - Material | Electrical | Electrical - Material | Design | Quality | Electrical - Material | Utilize material consignment with electrical bulk material suppliers (such as, General Electric, Graybar, etc.) | Tom Bullington (KBR)
1215 | Electrical - Material | Electrical | Electrical - Material | Design | Quality | Electrical - Material | Standardization of design installation details will enable early purchase of bulk items | Tom Bullington (KBR)
1216 | Electrical - Material | Electrical | Electrical - Material | Design | Quality | Electrical - Material | Control Station supports and all other supports that require Galvanized steel should be shop fabricated & Galvanized when possible. | Tom Bullington (KBR)
1217 | Electrical - Material | Electrical | Electrical - Material | Design | Quality | Electrical - Material | Ensure that Constructability reviews are performed on all design installation details to review bulk materials are covered on material lists | Tom Bullington (KBR)
1218 | Electrical - Material | Electrical | Electrical - Material | Design | Quality | Electrical - Material | The types of bulk materials shall be standardized to reduce the number of different sizes and/or materials. | Tom Bullington (KBR)
1219 | Electrical - Power | Electrical | Electrical - Power | Design | Quality | Electrical - Power | Pulling calculations should be part of the underground conduit design. | Tom Bullington (KBR)
1220 | Electrical - Power | Electrical | Electrical - Power | Design | Quality | Electrical - Power | Issue electrical underground drawings during civil phase and MUST be coordinated with construction schedule. Avoid routing water lines over U/G cable when possible. | Tom Bullington (KBR)
1221 | Electrical - Power | Electrical | Electrical - Power | Design | Quality | Electrical - Power | Long run multi-pair cable will be identified on the individual spools when they are shipped. | Tom Bullington (KBR)
1222 | Electrical - Power | Electrical | Electrical - Power | Design | Quality | Electrical - Power | For underground feeders with single conductor cable, purchase this cable on three reels. | Tom Bullington (KBR)
1223 | Electrical - Power | Electrical | Electrical - Power | Design | Quality | Electrical - Power | Adequate space must be considered for neat termination of cables in terminal boxes. | Tom Bullington (KBR)
1224 | Electrical - Power | Electrical | Electrical - Power | Design | Quality | Electrical - Power | Specify cable reels to be shipped in upright position, not on sides, for ease of unloading, and prevent cable damage. | Tom Bullington (KBR)
1225 | Electrical - Power | Electrical | Electrical - Power | Design | Quality | Electrical - Power | Provide adequate space in all cabinets, switchgear, etc., to allow for proper field installation of jacketed cable. | Tom Bullington (KBR)
1226 | Electrical - Power | Electrical | Electrical - Power | Design | Quality | Electrical - Power | Review reduction of minimum depth requirements for direct buried cables. | Tom Bullington (KBR)
1227 | Electrical - Power | Electrical | Electrical - Power | Design | Quality | Electrical - Power | Install pulling eye in bottom and sides of manholes (needed in bottom to hold down sheaves). | Tom Bullington (KBR)
1228 | Electrical - Power | Electrical | Electrical - Power | Design | Quality | Electrical - Power | Develop or use spreadsheet software for matching cable pulls with cable reels. | Tom Bullington (KBR)
1229 | Electrical - Power | Electrical | Electrical - Power | Design | Quality | Electrical - Power | Use color-coded wire on control cables. | Tom Bullington (KBR)
1230 | Electrical - Power | Electrical | Electrical - Power | Design | Quality | Electrical - Power | Engineering to provide cut length schedules for power cable. Lengths will include allowances for terminations. | Tom Bullington (KBR)
1231 | Electrical - Power | Electrical | Electrical - Power | Design | Quality | Electrical - Power | Standardize cable size. | Tom Bullington (KBR)
1232 | Electrical - Power | Electrical | Electrical - Power | Design | Quality | Electrical - Power | Consider over-sizing electrical cables to meet construction schedule delivery requirements instead of determination of every minor electrical load. | Tom Bullington (KBR)
1233 | Electrical - Power | Electrical | Electrical - Power | Design | Quality | Electrical - Power | Take steps to assure that circuit numbers for large sizes of electrical cable are identified on individual spools when they are shipped. | Tom Bullington (KBR)
1234 | Electrical - Power | Electrical | Electrical - Power | Design | Quality | Electrical - Power | Be sure power supply is adequate for all panel or skid mounted equipment. | Tom Bullington (KBR)
1235 | Electrical - Power | Electrical | Electrical - Power | Design | Quality | Electrical - Power | Make sure door openings are large enough to install equipment. | Tom Bullington (KBR)
1236 | Electrical - Power | Electrical | Electrical - Power | Design | Quality | Electrical - Power | Disconnect switches should be shown on drawings. | Tom Bullington (KBR)
1237 | Electrical - Power | Electrical | Electrical - Power | Design | Quality | Electrical - Power | Motor connection boxes should be large enough for bulky terminations, including stress relief devices. Indicate specific sizes on purchase requisitions rather than accepting standard NEMA sizes. Consider elastimold type connection (bushings) wired by supplier on large motors. Field to furnish elbow connections according to cable diameters for supplier furnished buildings. | Tom Bullington (KBR)
1238 | Electrical - Power | Electrical | Electrical - Power | Design | Quality | Electrical - Power | Design electrical heat trace to support piping installation schedules and reduce scaffolding requirements. Ensure excess wire and cable can be returned to supplier for credit by including the proper language in the purchase order. | Tom Bullington (KBR)
1239 | Electrical - Power | Electrical | Electrical - Power | Design | Quality | Electrical - Power | In high-risk areas, design high voltage electrical lines underground to minimize crane contact or pipe rack energization. | Tom Bullington (KBR)
1240 | Electrical - Power | Electrical | Electrical - Power | Design | Quality | Electrical - Power | Purchase cable with footage markers on outer jacket when possible. | Tom Bullington (KBR)
1241 | Electrical - Power | Electrical | Electrical - Power | Design | Quality | Electrical - Power | Assure field is made aware of equipment being received with impact meters attached. | Tom Bullington (KBR)
1242 | Electrical - Power | Electrical | Electrical - Power | Design | Quality | Electrical - Power | Consider the use of shrink sleeves for 600-volt control cable splices, when splices are authorized. | Tom Bullington (KBR)
1243 | Electrical - Power | Electrical | Electrical - Power | Design | Quality | Electrical - Power | Specify heat shrink or pre-molded stress relief devices for medium voltage cable termination. | Tom Bullington (KBR)
1244 | Electrical - Substation | Electrical | Electrical - Substation | Design | Quality | Electrical - Substation | Rigging for heavy transformers should be a pre-designed lift with a responsible rigging engineer looking at pick points and adequacy of lifting lugs in accordance with current BE&K Rigging Practices. | Tom Bullington (KBR)
1245 | Electrical - Substation | Electrical | Electrical - Substation | Design | Quality | Electrical - Substation | Design embedded floor channel (or block-outs) for supporting switchgear (in buildings) flush and level with top of floor to permit easy installation and removal of breakers. Slightly slope foundations for outside switchgear so that water will not pond around the gear. | Tom Bullington (KBR)
1246 | Electrical - Substation | Electrical | Electrical - Substation | Design | Quality | Electrical - Substation | Engineering needs to complete all design calculations for the high and low voltage relay settings and issue to field to meet substation check out schedule. | Tom Bullington (KBR)
1247 | Electrical - Temporary Power | Electrical | Electrical - Temporary Power | Design | Quality | Electrical - Temporary Power | Design and review of temporary power should be done jointly between engineering and construction to insure a safe project, cost effective and usable system. | Tom Bullington (KBR)
1248 | Electrical - Temporary Power | Electrical | Electrical - Temporary Power | Design | Quality | Electrical - Temporary Power | Insure that there is enough temporary power available for checkout and start-up or that permanent power will be available when the primary stages of start-up begin. | Tom Bullington (KBR)
1249 | Electrical - Temporary Power | Electrical | Electrical - Temporary Power | Design | Quality | Electrical - Temporary Power | To save money the temporary power system should utilize as much of the permanent system equipment as possible (i.e., transformers, lighting panels, etc.). | Tom Bullington (KBR)
1250 | Electrical - Temporary Power | Electrical | Electrical - Temporary Power | Design | Quality | Electrical - Temporary Power | Utilize twist lock plugs on temporary service. | Tom Bullington (KBR)
1251 | Electrical - Temporary Power | Electrical | Electrical - Temporary Power | Design | Quality | Electrical - Temporary Power | Insure that temporary power conforms to existing SHE practices. | Tom Bullington (KBR)
1252 | Electrical - Testing | Electrical | Electrical - Testing | Design | Quality | Electrical - Testing | Engineering to establish high voltage equipment and cable testing requirements to allow subcontract package for this specialized service. | Tom Bullington (KBR)
1253 | Electrical - Vendor Requirements | Electrical | Electrical - Vendor Requirements | Design | Quality | Electrical - Vendor Requirements | Engineering to issue interface drawings for multiple supplier equipment & specify individual vendor requirements. | Tom Bullington (KBR)
1254 | Electrical - Vendor Requirements | Electrical | Electrical - Vendor Requirements | Design | Quality | Electrical - Vendor Requirements | Require Vendors to comply with specifications for marking terminal blocks. | Tom Bullington (KBR)
1255 | Electrical - Vendor Requirements | Electrical | Electrical - Vendor Requirements | Design | Quality | Electrical - Vendor Requirements | Supplier to supplier connections must be carefully checked for compatibility (example: duct to switchgear). | Tom Bullington (KBR)
1256 | Electrical - Vendor Requirements | Electrical | Electrical - Vendor Requirements | Design | Quality | Electrical - Vendor Requirements | All specialized equipment should be shop inspected prior to shipment to the field. | Tom Bullington (KBR)
1257 | Electrical - Vendor Requirements | Electrical | Electrical - Vendor Requirements | Design | Quality | Electrical - Vendor Requirements | Pre-inspection meeting with equipment suppliers should be held very early. | Tom Bullington (KBR)
1258 | Electrical - Vendor Requirements | Electrical | Electrical - Vendor Requirements | Design | Quality | Electrical - Vendor Requirements | Project engineer should be assigned to coordinate major equipment suppliers. | Tom Bullington (KBR)
1259 | Electrical - Vendor Requirements | Electrical | Electrical - Vendor Requirements | Design | Quality | Electrical - Vendor Requirements | Consider operator and maintenance personnel training courses before the purchase of sophisticated machinery. (Sometimes a supplier or manufacturer will provide free training to make the sale). | Tom Bullington (KBR)
1260 | Electrical - Vendor Requirements | Electrical | Electrical - Vendor Requirements | Design | Quality | Electrical - Vendor Requirements | Supplier skids must specify NEC code requirements clearly. Supplier skids should be inspected prior to leaving shop. Much electrical rework is associated with skids. | Tom Bullington (KBR)
1261 | Electrical - Vendor Requirements | Electrical | Electrical - Vendor Requirements | Design | Quality | Electrical - Vendor Requirements | Plan to use supplier representative on major pieces of electrical equipment; include field terms and conditions in P.O. | Tom Bullington (KBR)
1262 | Mechanical Equipment - Cleaning | Mechanical | Mechanical Equipment - Cleaning | Design | Quality | Mechanical Equipment - Cleaning | Provide early requirements for chemical cleaning. | Tom Bullington (KBR)
1263 | Mechanical Equipment - Cleaning | Mechanical | Mechanical Equipment - Cleaning | Design | Quality | Mechanical Equipment - Cleaning | Review provisions for preventing cross-contamination. | Tom Bullington (KBR)
1264 | Mechanical Equipment - Drawings & Specifications | Mechanical | Mechanical Equipment - Drawings & Specifications | Design | Quality | Mechanical Equipment - Drawings & Specifications | Consider including all required information in equipment specifications. Do not refer suppliers to general specifications, insulation specifications or painting specifications. | Tom Bullington (KBR)
1265 | Mechanical Equipment - Drawings & Specifications | Mechanical | Mechanical Equipment - Drawings & Specifications | Design | Quality | Mechanical Equipment - Drawings & Specifications | Ensure that equipment list includes requirements for painting, insulation and fireproofing of equipment. | Tom Bullington (KBR)
1266 | Mechanical Equipment - Drawings & Specifications | Mechanical | Mechanical Equipment - Drawings & Specifications | Design | Quality | Mechanical Equipment - Drawings & Specifications | Ensure supplier prints reproduced from sepias are clear and readable before they are transmitted to the field. | Tom Bullington (KBR)
1267 | Mechanical Equipment - Exchangers | Mechanical | Mechanical Equipment - Exchangers | Design | Quality | Mechanical Equipment - Exchangers | Whenever slide bases such as at exchanger supports are required, design and procure to coincide with foundation installation schedule. | Tom Bullington (KBR)
1268 | Mechanical Equipment - Exchangers | Mechanical | Mechanical Equipment - Exchangers | Design | Quality | Mechanical Equipment - Exchangers | Coordinate purchase of refractory materials so that fresh materials are being used. Follow supplier's recommendations on installation. | Tom Bullington (KBR)
1269 | Mechanical Equipment - Exchangers | Mechanical | Mechanical Equipment - Exchangers | Design | Quality | Mechanical Equipment - Exchangers | Evaluate cooling tower materials such as treated wood, concrete, fiberglass, galvanized steel, stainless steel and ceramics to optimize costs for material, labor and maintenance. | Tom Bullington (KBR)
1270 | Mechanical Equipment - Exchangers | Mechanical | Mechanical Equipment - Exchangers | Design | Quality | Mechanical Equipment - Exchangers | Design for heat exchangers should include lifting lugs and removable heads. Installed these items on equipment while in the fabrication shop or facility. | Tom Bullington (KBR)
1271 | Mechanical Equipment - Exchangers | Mechanical | Mechanical Equipment - Exchangers | Design | Quality | Mechanical Equipment - Exchangers | When possible, modularize large pieces of equipment such as furnaces and boilers. | Tom Bullington (KBR)
1272 | Mechanical Equipment - Exchangers | Mechanical | Mechanical Equipment - Exchangers | Design | Quality | Mechanical Equipment - Exchangers | Ensure that the area required for tube bundle removal is clearly indicated on the equipment arrangement, mechanical and piping drawings. Ensure that circulating water and other piping are designed for ease of removal in these areas. | Tom Bullington (KBR)
1273 | Mechanical Equipment - Expediting | Mechanical | Mechanical Equipment - Expediting | Design | Quality | Mechanical Equipment - Expediting | Test run all new equipment at the factory whenever possible. Test results should become a permanent part of supplier documentation. | Tom Bullington (KBR)
1274 | Mechanical Equipment - Expediting | Mechanical | Mechanical Equipment - Expediting | Design | Quality | Mechanical Equipment - Expediting | Issue project specifications for plumb / level / alignment of vessels early in project. (i.e., level by trays at shop) | Tom Bullington (KBR)
1275 | Mechanical Equipment - Expediting | Mechanical | Mechanical Equipment - Expediting | Design | Quality | Mechanical Equipment - Expediting | Review equipment for complete supplier documentation (i.e. parts lists, recommended spares, predictive maintenance specifications, repair manuals and design specifications | Tom Bullington (KBR)
1276 | Mechanical Equipment - Expediting | Mechanical | Mechanical Equipment - Expediting | Design | Quality | Mechanical Equipment - Expediting | Review equipment for factory spare parts policy. | Tom Bullington (KBR)
1277 | Mechanical Equipment - Expediting | Mechanical | Mechanical Equipment - Expediting | Design | Quality | Mechanical Equipment - Expediting | Review equipment for commissioning spares and initial operating spares with original equipment purchase | Tom Bullington (KBR)
1278 | Mechanical Equipment - Expediting | Mechanical | Mechanical Equipment - Expediting | Design | Quality | Mechanical Equipment - Expediting | Review equipment for extended warranties for up to 12 month after start-up, when possible | Tom Bullington (KBR)
1279 | Mechanical Equipment - Expediting | Mechanical | Mechanical Equipment - Expediting | Design | Quality | Mechanical Equipment - Expediting | Review each piece of equipment in the SHOP to ensure as much work as possible is completed by vendor (i.e. vessel internals, pre-assembly, etc.) | Tom Bullington (KBR)
1280 | Mechanical Equipment - Expediting | Mechanical | Mechanical Equipment - Expediting | Design | Quality | Mechanical Equipment - Expediting | Ensure that ALL stress relieved equipment is clearly marked prior to leaving shop. | Tom Bullington (KBR)
1281 | Mechanical Equipment - Expediting | Mechanical | Mechanical Equipment - Expediting | Design | Quality | Mechanical Equipment - Expediting | Agree to a master equipment numbering system before ordering plant equipment. The supplier (or factory) should be responsible for tagging all equipment. All associated vendor documentation should include reference to the Master Equipment List number. | Tom Bullington (KBR)
1282 | Mechanical Equipment - General | Mechanical | Mechanical Equipment - General | Design | Quality | Mechanical Equipment - General | Equipment standardization for a project is critical. Major equipment often does not lend itself to standardization but minor equipment does; i.e., controls, electrical components, valves, tubing fittings, small pumps, hydraulic motors and couplings. Note: Standardization reduces spare part requirements and maintenance personnel training. | Tom Bullington (KBR)
1283 | Mechanical Equipment - Instruments | Mechanical | Mechanical Equipment - Instruments | Design | Quality | Mechanical Equipment - Instruments | Keep instrumentation and operation valves outside noise enclosures. | Tom Bullington (KBR)
1284 | Mechanical Equipment - Insulation & Coatings | Mechanical | Mechanical Equipment - Insulation & Coatings | Design | Quality | Mechanical Equipment - Insulation & Coatings | Ensure finish painting of vessels and equipment in vendor's shop. | Tom Bullington (KBR)
1285 | Mechanical Equipment - Insulation & Coatings | Mechanical | Mechanical Equipment - Insulation & Coatings | Design | Quality | Mechanical Equipment - Insulation & Coatings | Shop-apply fireproofing / painting / internal coatings where practical. | Tom Bullington (KBR)
1286 | Mechanical Equipment - Insulation & Coatings | Mechanical | Mechanical Equipment - Insulation & Coatings | Design | Quality | Mechanical Equipment - Insulation & Coatings | Provide sufficient clearance between insulation jacketing, platforms, ladders, pipe guides, etc. | Tom Bullington (KBR)
1287 | Mechanical Equipment - Insulation & Coatings | Mechanical | Mechanical Equipment - Insulation & Coatings | Design | Quality | Mechanical Equipment - Insulation & Coatings | Equipment list should list requirements for painting, insulation and fireproofing. | Tom Bullington (KBR)
1288 | Mechanical Equipment - Pre-Assembly | Mechanical | Mechanical Equipment - Pre-Assembly | Design | Quality | Mechanical Equipment - Pre-Assembly | Encourage requirements for shop assembly, match marking and dismantling of equipment that may have fit-up problems. | Tom Bullington (KBR)
1289 | Mechanical Equipment - Procurement & Expediting | Mechanical | Mechanical Equipment - Procurement & Expediting | Design | Quality | Mechanical Equipment - Procurement & Expediting | Provide shop and field inspection criteria for all process equipment. | Tom Bullington (KBR)
1290 | Mechanical Equipment - Procurement & Expediting | Mechanical | Mechanical Equipment - Procurement & Expediting | Design | Quality | Mechanical Equipment - Procurement & Expediting | Require bill of materials and supplier's drawings for equipment supplied prior to or at time of equipment delivery. Ensure items such as gaskets and bolts are included in bill of materials and shipping lists. | Tom Bullington (KBR)
1291 | Mechanical Equipment - Procurement & Expediting | Mechanical | Mechanical Equipment - Procurement & Expediting | Design | Quality | Mechanical Equipment - Procurement & Expediting | Select equipment based on total installed cost and not just on initial purchase price. | Tom Bullington (KBR)
1292 | Mechanical Equipment - Procurement & Expediting | Mechanical | Mechanical Equipment - Procurement & Expediting | Design | Quality | Mechanical Equipment - Procurement & Expediting | Provide engineering in supplier's facilities when required to assure fabrication approvals, material ordering and fabrication schedules are not impaired. | Tom Bullington (KBR)
1293 | Mechanical Equipment - Procurement & Expediting | Mechanical | Mechanical Equipment - Procurement & Expediting | Design | Quality | Mechanical Equipment - Procurement & Expediting | Consider the U.S. might not be a viable source at this time for vessels with wall thickness of 5" or greater. | Tom Bullington (KBR)
1294 | Mechanical Equipment - Procurement & Expediting | Mechanical | Mechanical Equipment - Procurement & Expediting | Design | Quality | Mechanical Equipment - Procurement & Expediting | Consider vessel grouping for fabrication and go to one supplier and/or a geographical location. | Tom Bullington (KBR)
1295 | Mechanical Equipment - Procurement & Expediting | Mechanical | Mechanical Equipment - Procurement & Expediting | Design | Quality | Mechanical Equipment - Procurement & Expediting | Develop list of preferred suppliers | Tom Bullington (KBR)
1296 | Mechanical Equipment - Procurement & Expediting | Mechanical | Mechanical Equipment - Procurement & Expediting | Design | Quality | Mechanical Equipment - Procurement & Expediting | Review past experience and record from supplier evaluations | Tom Bullington (KBR)
1297 | Mechanical Equipment - Procurement & Expediting | Mechanical | Mechanical Equipment - Procurement & Expediting | Design | Quality | Mechanical Equipment - Procurement & Expediting | Identify and specify marking for vessel internal materials such as balls, clips, trays and sheds. Instruct fabricators and inspection to package, install, ship and otherwise keep separate all such materials. | Tom Bullington (KBR)
1298 | Mechanical Equipment - Procurement & Expediting | Mechanical | Mechanical Equipment - Procurement & Expediting | Design | Quality | Mechanical Equipment - Procurement & Expediting | Establish a program to expedite, receive, catalog, file and distribute all requested documentation during the project. "Holdbacks" should be negotiated with equipment suppliers to ensure compliance with document requests. After start-up and turnover, one or more complete master sets of data should be formally transmitted to [Client]. | Tom Bullington (KBR)
1299 | Mechanical Equipment - Procurement & Expediting | Mechanical | Mechanical Equipment - Procurement & Expediting | Design | Quality | Mechanical Equipment - Procurement & Expediting | Some air permits require extended warranty and service periods on pollution control equipment. Determine how to provide for such under the original purchase order or alternate means. Make a general statement for items where an extended warranty is required or desired. | Tom Bullington (KBR)
1300 | Mechanical Equipment - Pumps, Compressors & Rotating Equipment | Mechanical | Mechanical Equipment - Pumps, Compressors & Rotating Equipment | Design | Quality | Mechanical Equipment - Pumps, Compressors & Rotating Equipment | Show all pump seal water requirements on separate pump trim drawings with the type of service connection requirements, instrumentation (FI, PI) and valves. | Tom Bullington (KBR)
1301 | Mechanical Equipment - Pumps, Compressors & Rotating Equipment | Mechanical | Mechanical Equipment - Pumps, Compressors & Rotating Equipment | Design | Quality | Mechanical Equipment - Pumps, Compressors & Rotating Equipment | Shop-mount direct coupled pumps and motors where possible. | Tom Bullington (KBR)
1302 | Mechanical Equipment - Pumps, Compressors & Rotating Equipment | Mechanical | Mechanical Equipment - Pumps, Compressors & Rotating Equipment | Design | Quality | Mechanical Equipment - Pumps, Compressors & Rotating Equipment | Establish requirements for supplier's technical assistance for erection, start-up and run-in of equipment and include requirements in purchase orders. | Tom Bullington (KBR)
1303 | Mechanical Equipment - Pumps, Compressors & Rotating Equipment | Mechanical | Mechanical Equipment - Pumps, Compressors & Rotating Equipment | Design | Quality | Mechanical Equipment - Pumps, Compressors & Rotating Equipment | Ship bolts, gaskets, etc. with equipment not only for construction but also commissioning and start-up spares. | Tom Bullington (KBR)
1304 | Mechanical Equipment - Pumps, Compressors & Rotating Equipment | Mechanical | Mechanical Equipment - Pumps, Compressors & Rotating Equipment | Design | Quality | Mechanical Equipment - Pumps, Compressors & Rotating Equipment | Ensure that base plates have adequate size and number of ports for adequate grouting. | Tom Bullington (KBR)
1305 | Mechanical Equipment - Pumps, Compressors & Rotating Equipment | Mechanical | Mechanical Equipment - Pumps, Compressors & Rotating Equipment | Design | Quality | Mechanical Equipment - Pumps, Compressors & Rotating Equipment | Clearly define on the drawings all alignment tolerances, hot and cold, where required. | Tom Bullington (KBR)
1306 | Mechanical Equipment - Pumps, Compressors & Rotating Equipment | Mechanical | Mechanical Equipment - Pumps, Compressors & Rotating Equipment | Design | Quality | Mechanical Equipment - Pumps, Compressors & Rotating Equipment | Maximize the use of in-line pumps when process and specifications allow. | Tom Bullington (KBR)
1307 | Mechanical Equipment - Pumps, Compressors & Rotating Equipment | Mechanical | Mechanical Equipment - Pumps, Compressors & Rotating Equipment | Design | Quality | Mechanical Equipment - Pumps, Compressors & Rotating Equipment | Consider maintenance requirements when designing equipment layouts. Allow adequate space to isolate one piece of equipment for maintenance activities while nearby equipment remains in service. Some hazardous operation areas require special design such as double block and bleed (dual blind pipe flanges) in addition to normal valves on compressor piping. | Tom Bullington (KBR)
1308 | Mechanical Equipment - Safety | Mechanical | Mechanical Equipment - Safety | Design | Safety | Mechanical Equipment - Safety | Determine safety requirements on all equipment; i.e., gears, chains, belts, hot equipment, toxic fumes, and radioactivity. (Guards must be easily removable for maintenance). Study supplier documents and consult with safety professionals. | Tom Bullington (KBR)
1309 | Mechanical Equipment - Safety | Mechanical | Mechanical Equipment - Safety | Design | Safety | Mechanical Equipment - Safety | Consider the need for special protective equipment and clothing. Study supplier documents for requirements. | Tom Bullington (KBR)
1310 | Mechanical Equipment - Safety | Mechanical | Mechanical Equipment - Safety | Design | Safety | Mechanical Equipment - Safety | Refer to manufacturer's operating specifications and define maximum / minimum limits of equipment performance. | Tom Bullington (KBR)
1311 | Mechanical Equipment - Safety | Mechanical | Mechanical Equipment - Safety | Design | Safety | Mechanical Equipment - Safety | Determine equipment and / or processes that can be operated beyond design limits. Install fail-safe limiting devices. | Tom Bullington (KBR)
1312 | Mechanical Equipment - Safety | Mechanical | Mechanical Equipment - Safety | Design | Safety | Mechanical Equipment - Safety | Engineer must detail equipment guards for large rotating equipment. | Tom Bullington (KBR)
1313 | Mechanical Equipment - Scheduling | Mechanical | Mechanical Equipment - Scheduling | Project Control | Schedule Performance | Mechanical Equipment - Scheduling | When machined surfaces are required for an item, check with Engineering before welding on any machined item. Specify desired quality or grade of machined surfaces) on applicable drawings. Also, indicate if machining is to be done after fabrication in shop. | Tom Bullington (KBR)
1314 | Mechanical Equipment - Scheduling | Mechanical | Mechanical Equipment - Scheduling | Project Control | Schedule Performance | Mechanical Equipment - Scheduling | Verify that piping checks all final nozzle locations prior to drawing approval and fabrication. | Tom Bullington (KBR)
1315 | Mechanical Equipment - Scheduling | Mechanical | Mechanical Equipment - Scheduling | Project Control | Schedule Performance | Mechanical Equipment - Scheduling | Identify portions of mechanical work that can be worked early to release-related piping, electrical and instrumentation items, thus relieving later peaking of critical craft loading. | Tom Bullington (KBR)
1316 | Mechanical Equipment - Scheduling | Mechanical | Mechanical Equipment - Scheduling | Project Control | Schedule Performance | Mechanical Equipment - Scheduling | Consider schedule deliveries of weather sensitive equipment and materials within reasonable periods of construction needs. | Tom Bullington (KBR)
1317 | Mechanical Equipment - Scheduling | Mechanical | Mechanical Equipment - Scheduling | Project Control | Schedule Performance | Mechanical Equipment - Scheduling | Large transfer lines, slide valves and like items must be engineered and fabricated for installation incrementally with the structure and vessels. | Tom Bullington (KBR)
1318 | Mechanical Equipment - Scheduling | Mechanical | Mechanical Equipment - Scheduling | Project Control | Schedule Performance | Mechanical Equipment - Scheduling | Give priority to oil mist systems so that rotating equipment can be run prior to mechanical and electrical completion, if needed. | Tom Bullington (KBR)
1319 | Mechanical Equipment - Skid Mounted Equipment | Mechanical | Mechanical Equipment - Skid Mounted Equipment | Design | Quality | Mechanical Equipment - Skid Mounted Equipment | Ensure drainage system for skid-mounted equipment has been included in the design drawings and specifications. | Tom Bullington (KBR)
1320 | Mechanical Equipment - Skid Mounted Equipment | Mechanical | Mechanical Equipment - Skid Mounted Equipment | Design | Quality | Mechanical Equipment - Skid Mounted Equipment | Specify major equipment skids such as turbines with lube oil systems integrated as part of the skid so that oil flush can be performed in the shop. | Tom Bullington (KBR)
1321 | Mechanical Equipment - Skid Mounted Equipment | Mechanical | Mechanical Equipment - Skid Mounted Equipment | Design | Quality | Mechanical Equipment - Skid Mounted Equipment | Ensure that skid mounted equipment has adequate framing to prevent warping during shipment. | Tom Bullington (KBR)
1322 | Mechanical Equipment - Start-up | Mechanical | Mechanical Equipment - Start-up | Design | Quality | Mechanical Equipment - Start-up | Ship bolts, gaskets, etc., with equipment not only for construction but also commissioning and start-up spares | Tom Bullington (KBR)
1323 | Mechanical Equipment - Storage & Maintenance | Mechanical | Mechanical Equipment - Storage & Maintenance | Design | Quality | Mechanical Equipment - Storage & Maintenance | Provide procedures for preventive maintenance of items in storage as well as installed items prior to start-up. | Tom Bullington (KBR)
1324 | Mechanical Equipment - Storage & Maintenance | Mechanical | Mechanical Equipment - Storage & Maintenance | Design | Quality | Mechanical Equipment - Storage & Maintenance | Issue a complete lube oil and lubrication schedule prior to arrival at job site of first rotating equipment. Consider preliminary issue if required. This must include the owner's requirements as well. | Tom Bullington (KBR)
1325 | Mechanical Equipment - Storage & Maintenance | Mechanical | Mechanical Equipment - Storage & Maintenance | Design | Quality | Mechanical Equipment - Storage & Maintenance | Engineering should expedite supplier's operation, installation and maintenance manuals for packaged systems, pumps, compressors, agitators and other rotating equipment to ensure availability prior to receipt of the equipment. | Tom Bullington (KBR)
1326 | Mechanical Equipment - Storage & Maintenance | Mechanical | Mechanical Equipment - Storage & Maintenance | Design | Quality | Mechanical Equipment - Storage & Maintenance | Ensure that flange protection is provided during shipping, storage and installation of all vessels. | Tom Bullington (KBR)
1327 | Mechanical Equipment - Storage & Maintenance | Mechanical | Mechanical Equipment - Storage & Maintenance | Design | Quality | Mechanical Equipment - Storage & Maintenance | Consider maintenance accessibility in the final decision on all equipment locations and equipment accessories like control cabinets, valves, power units and filters. | Tom Bullington (KBR)
1328 | Mechanical Equipment - Storage & Maintenance | Mechanical | Mechanical Equipment - Storage & Maintenance | Design | Quality | Mechanical Equipment - Storage & Maintenance | Perform a Reliability Centered Maintenance analysis on equipment. | Tom Bullington (KBR)
1329 | Mechanical Equipment - Storage & Maintenance | Mechanical | Mechanical Equipment - Storage & Maintenance | Design | Quality | Mechanical Equipment - Storage & Maintenance | Consider long-term repair costs and potential equipment downtime when approving plant equipment specifications; i.e., built-in lubrication systems, waterproof motor instead of standard types, alloy materials instead of coatings, corrosion resistant materials in wash down areas and non-friable insulating materials in high heat areas. | Tom Bullington (KBR)
1330 | Mechanical Equipment - Transportation, Lifting & Handling | Mechanical | Mechanical Equipment - Transportation, Lifting & Handling | Design | Quality | Mechanical Equipment - Transportation, Lifting & Handling | Require in bid specifications that supplier / vendor design and provide any special lifting beams for equipment or components required for lifts. Especially for condensers, turbines and dryers. Require that these required components be shipped to the site for delivery prior to equipment arrival. | Tom Bullington (KBR)
1331 | Mechanical Equipment - Transportation, Lifting & Handling | Mechanical | Mechanical Equipment - Transportation, Lifting & Handling | Design | Quality | Mechanical Equipment - Transportation, Lifting & Handling | Have vendors provide erection procedures for compressors, pumps, stacks, or any special lifting requirements. Ensure that material requisitions require this. | Tom Bullington (KBR)
1332 | Mechanical Equipment - Transportation, Lifting & Handling | Mechanical | Mechanical Equipment - Transportation, Lifting & Handling | Design | Quality | Mechanical Equipment - Transportation, Lifting & Handling | Specify jacking pockets for shipping saddles so non-hydraulic trailers can be utilized. | Tom Bullington (KBR)
1333 | Mechanical Equipment - Transportation, Lifting & Handling | Mechanical | Mechanical Equipment - Transportation, Lifting & Handling | Design | Quality | Mechanical Equipment - Transportation, Lifting & Handling | Ship vessels with lifting lugs located so that vessels do not have to be rolled / re-oriented at site. Take in consideration insulation thickness and weight in lifting lugs design to have equipment insulated in horizontal position prior to setting. Specify on drawings lifting and ground lug removal plan if required. | Tom Bullington (KBR)
1334 | Mechanical Equipment - Transportation, Lifting & Handling | Mechanical | Mechanical Equipment - Transportation, Lifting & Handling | Design | Quality | Mechanical Equipment - Transportation, Lifting & Handling | Place center of gravity (CG) & shipping weight on all vessels, particularly horizontal equipment (tanks, bullets, etc.). | Tom Bullington (KBR)
1335 | Mechanical Equipment - Transportation, Lifting & Handling | Mechanical | Mechanical Equipment - Transportation, Lifting & Handling | Design | Quality | Mechanical Equipment - Transportation, Lifting & Handling | If equipment locations are revised or other revisions affecting rigging plans occur, ensure that the flow of information between design and construction is executed expeditiously. | Tom Bullington (KBR)
1336 | Mechanical Equipment - Transportation, Lifting & Handling | Mechanical | Mechanical Equipment - Transportation, Lifting & Handling | Design | Quality | Mechanical Equipment - Transportation, Lifting & Handling | Specify ALL shipping attachments and temporary bracing are clearly marked (i.e. painted orange) for removal after erection. | Tom Bullington (KBR)
1337 | Mechanical Equipment - Transportation, Lifting & Handling | Mechanical | Mechanical Equipment - Transportation, Lifting & Handling | Design | Quality | Mechanical Equipment - Transportation, Lifting & Handling | As early as possible, the Engineer should provide the following information to formulate a Preliminary Master Rigging Plan: Equipment list with weights and dimensions, plot plans, equipment drawings and proposed mode of transportation & delivery schedule | Tom Bullington (KBR)
1338 | Mechanical Equipment - Transportation, Lifting & Handling | Mechanical | Mechanical Equipment - Transportation, Lifting & Handling | Design | Quality | Mechanical Equipment - Transportation, Lifting & Handling | Clearly define all test procedures for overhead cranes and other mechanical handling equipment. | Tom Bullington (KBR)
1339 | Mechanical Equipment - Transportation, Lifting & Handling | Mechanical | Mechanical Equipment - Transportation, Lifting & Handling | Design | Quality | Mechanical Equipment - Transportation, Lifting & Handling | Study the effect of crane and other equipment movements upon the permissible density of workers in congested areas and plan shift work to relieve overload problems with either equipment or people. | Tom Bullington (KBR)
1340 | Mechanical Equipment - Vessels | Mechanical | Mechanical Equipment - Vessels | Design | Quality | Mechanical Equipment - Vessels | Use anchor bolt / base plate templates from vessel fabricator (vessels 48' & larger) to facilitate accurate placement of the bolts in the foundation. | Tom Bullington (KBR)
1341 | Mechanical Equipment - Vessels | Mechanical | Mechanical Equipment - Vessels | Design | Quality | Mechanical Equipment - Vessels | Analyze vessels for any special shipping requirements. Provide roundup ring girders or other bracing if required. | Tom Bullington (KBR)
1342 | Mechanical Equipment - Vessels | Mechanical | Mechanical Equipment - Vessels | Design | Quality | Mechanical Equipment - Vessels | Indicate minimum pressurizing temperatures (ambient, vessel and water) for hydro testing. | Tom Bullington (KBR)
1343 | Mechanical Equipment - Vessels | Mechanical | Mechanical Equipment - Vessels | Design | Quality | Mechanical Equipment - Vessels | Consider equipment pre-assembly prior to setting. For example, install handrails, platforms and apply insulation and paint. Design stacks with flanged connections if possible. | Tom Bullington (KBR)
1344 | Mechanical Equipment - Vessels | Mechanical | Mechanical Equipment - Vessels | Design | Quality | Mechanical Equipment - Vessels | If at all possible, vessels with cyclones should be engineered for erection with the cyclones installed into the head at ground level and lifted as a completed assembly. | Tom Bullington (KBR)
1345 | Mechanical Equipment - Vessels | Mechanical | Mechanical Equipment - Vessels | Design | Quality | Mechanical Equipment - Vessels | Verify that dimensional tolerances are correctly specified and fabricated for trays and internals. | Tom Bullington (KBR)
1346 | Mechanical Equipment - Vessels | Mechanical | Mechanical Equipment - Vessels | Design | Quality | Mechanical Equipment - Vessels | Perform a cost analysis before specifying carbon steel tanks with interior coating. | Tom Bullington (KBR)
1347 | Mechanical Equipment - Vessels | Mechanical | Mechanical Equipment - Vessels | Design | Quality | Mechanical Equipment - Vessels | Provide shop installed crimped bar for insulation support on bottom heads and inside skirts. | Tom Bullington (KBR)
1348 | Mechanical Equipment - Vessels | Mechanical | Mechanical Equipment - Vessels | Design | Quality | Mechanical Equipment - Vessels | Check project requirements for fireproofing inside of vessel skirts. Eliminate by having only one opening in skirt. | Tom Bullington (KBR)
1349 | Mechanical Equipment - Vessels | Mechanical | Mechanical Equipment - Vessels | Design | Quality | Mechanical Equipment - Vessels | Provide sufficient clearance between items such as insulation jacketing and platforms, ladders and piping guides. | Tom Bullington (KBR)
1350 | Mechanical Equipment - Vessels | Mechanical | Mechanical Equipment - Vessels | Design | Quality | Mechanical Equipment - Vessels | Provide grounding lugs on all tanks and equipment for field installation of grounding cables especially anything with a protective interior lining. Orient equipment and lugs for embedded grounding termination. | Tom Bullington (KBR)
1351 | Mechanical Equipment - Vessels | Mechanical | Mechanical Equipment - Vessels | Design | Quality | Mechanical Equipment - Vessels | Develop ladder and platform drawings early in the design in order to support installation before erection of the vessel. Have vessel platforms fabricated to the fullest extent possible. | Tom Bullington (KBR)
1352 | Piping - Bolts & Gaskets | Mechanical | Piping - Bolts & Gaskets | Design | Quality | Piping - Bolts & Gaskets | Clearly specify any requirements for coating of stud bolts (i.e. grease, lubricant, paint / don't paint, etc.). | Tom Bullington (KBR)
1353 | Piping - Bolts & Gaskets | Mechanical | Piping - Bolts & Gaskets | Design | Quality | Piping - Bolts & Gaskets | Review specifications to minimize the number of different types of gaskets and bolting. Develop color-coding system for vendor to apply prior to field receiving in field for bolts and gaskets. | Tom Bullington (KBR)
1354 | Piping - Design Considerations | Mechanical | Piping - Design Considerations | Design | Quality | Piping - Design Considerations | Perform adequate checks on pipe supports at rotating equipment to ensure that no load is imposed on nozzles during construction or operation to disrupt alignment. | Tom Bullington (KBR)
1355 | Piping - Design Considerations | Mechanical | Piping - Design Considerations | Design | Quality | Piping - Design Considerations | Design should review vendor equipment drawings where equipment interfaces with piping. Items to be considered are pipe diameter, schedule, material and location of connection. | Tom Bullington (KBR)
1356 | Piping - Design Considerations | Mechanical | Piping - Design Considerations | Design | Quality | Piping - Design Considerations | Spring hangers (and heavy rod hangers) should be concentric with beam centerline. | Tom Bullington (KBR)
1357 | Piping - Design Considerations | Mechanical | Piping - Design Considerations | Design | Quality | Piping - Design Considerations | Be alert to two-phase flow lines - check for vibrations and support. Ensure multiple interfaces with Structural Engineer. | Tom Bullington (KBR)
1358 | Piping - Design Considerations | Mechanical | Piping - Design Considerations | Design | Quality | Piping - Design Considerations | Don't overlook checking hot and cold system piping for adequate flexibility and support. | Tom Bullington (KBR)
1359 | Piping - Design Considerations | Mechanical | Piping - Design Considerations | Design | Quality | Piping - Design Considerations | Plan to use as many permanent plant piping networks as practical for construction lines, even if this means temporarily changing services and fluids carried and tying into temporary lines. | Tom Bullington (KBR)
1360 | Piping - Design Considerations | Mechanical | Piping - Design Considerations | Design | Quality | Piping - Design Considerations | Expansion joints for rack piping runs should be nested together in a common location, when possible. | Tom Bullington (KBR)
1361 | Piping - Design Considerations | Mechanical | Piping - Design Considerations | Design | Quality | Piping - Design Considerations | Minimize the gap between the issuance of revised Flowsheets. The issuance of revised ISO's and orthographic drawings (if required). | Tom Bullington (KBR)
1362 | Piping - Design Considerations | Mechanical | Piping - Design Considerations | Design | Quality | Piping - Design Considerations | Standardize piping sub-assemblies for items such as: steam traps, utility stations, sample points, control valve stations, etc. so they can be pre-fabricated. | Tom Bullington (KBR)
1363 | Piping - Design Considerations | Mechanical | Piping - Design Considerations | Design | Quality | Piping - Design Considerations | Check economics of reducing block valves at pumps. | Tom Bullington (KBR)
1364 | Piping - Design Considerations | Mechanical | Piping - Design Considerations | Design | Quality | Piping - Design Considerations | Review valve locations on ASME BPVC piping to reduce the amount of code piping where this is cost effective. | Tom Bullington (KBR)
1365 | Piping - Design Considerations | Mechanical | Piping - Design Considerations | Design | Quality | Piping - Design Considerations | Evaluate for each job whether fittings for branch connections should be shop fabricated with the header or on the lateral spools. The evaluation should consider the length of pipe rack, size of pipe, number of laterals and accuracy of design. As general rule, all branch connections should stop at the header for shop fabrication. For rack stuffing piping laterals utilizing weld in tees or weld-o-lets should have such fitting welded to lateral spools / not to headers. | Tom Bullington (KBR)
1366 | Piping - Design Considerations | Mechanical | Piping - Design Considerations | Design | Quality | Piping - Design Considerations | Check equipment flange bolt holes for correct orientation / straddle of centerline. Check equipment at suppliers before shipment. Use slip on flange at vessel connections - field welded to ensure correct orientation. | Tom Bullington (KBR)
1367 | Piping - Design Considerations | Mechanical | Piping - Design Considerations | Design | Quality | Piping - Design Considerations | Do not use screwed piping for any system larger than 2-inches. | Tom Bullington (KBR)
1368 | Piping - Design Considerations | Mechanical | Piping - Design Considerations | Design | Quality | Piping - Design Considerations | Install valves for service pipe at 20', 40' or 60' intervals. | Tom Bullington (KBR)
1369 | Piping - Design Considerations | Mechanical | Piping - Design Considerations | Design | Quality | Piping - Design Considerations | Detail all pipe penetration on elevated structures to show field welds above (4’ above preferred) floor levels to minimize scaffolds. | Tom Bullington (KBR)
1370 | Piping - Design Considerations | Mechanical | Piping - Design Considerations | Design | Quality | Piping - Design Considerations | Install unions / flanges near all critical valves to facilitate removal and replacement for maintenance. | Tom Bullington (KBR)
1371 | Piping - Design Considerations | Mechanical | Piping - Design Considerations | Design | Quality | Piping - Design Considerations | Size the weep nipples from reinforcing pads to accommodate the thickness of insulation on the pipe or vessel involved. | Tom Bullington (KBR)
1372 | Piping - Drawings, Specification & Electronic Models | Mechanical | Piping - Drawings, Specification & Electronic Models | Design | Quality | Piping - Drawings, Specification & Electronic Models | "Rack stuffing" piping should be shown on Isometrics with a dotted line and field welds shown where shop fabricated spools connect to rack stuffing. | Tom Bullington (KBR)
1373 | Piping - Drawings, Specification & Electronic Models | Mechanical | Piping - Drawings, Specification & Electronic Models | Design | Quality | Piping - Drawings, Specification & Electronic Models | Engineering should establish clear coordinates on piping and electrical design drawings for fire protection piping and sprinklers. | Tom Bullington (KBR)
1374 | Piping - Drawings, Specification & Electronic Models | Mechanical | Piping - Drawings, Specification & Electronic Models | Design | Quality | Piping - Drawings, Specification & Electronic Models | Pipe specifications must include all needed information in one document. Do not refer vendors to general specifications, insulation, painting specifications, etc. | Tom Bullington (KBR)
1375 | Piping - Drawings, Specification & Electronic Models | Mechanical | Piping - Drawings, Specification & Electronic Models | Design | Quality | Piping - Drawings, Specification & Electronic Models | Piping isometrics and orthographic drawings should include all hydro test and process vents and drains. | Tom Bullington (KBR)
1376 | Piping - Drawings, Specification & Electronic Models | Mechanical | Piping - Drawings, Specification & Electronic Models | Design | Quality | Piping - Drawings, Specification & Electronic Models | All isometrics should have a detailed bill of material. Such bill of material should differentiate between shop fabrication and field fabrication and should be issued with the isometric. | Tom Bullington (KBR)
1377 | Piping - Drawings, Specification & Electronic Models | Mechanical | Piping - Drawings, Specification & Electronic Models | Design | Quality | Piping - Drawings, Specification & Electronic Models | Detail all pipes penetrating elevated structures. | Tom Bullington (KBR)
1378 | Piping - Drawings, Specification & Electronic Models | Mechanical | Piping - Drawings, Specification & Electronic Models | Design | Quality | Piping - Drawings, Specification & Electronic Models | Original isometrics of small and large bore pipe, after being prepared by design, should be maintained at the job site when "as built" drawings are required (especially ASME piping). Jobsite authority should be provided regarding changes. | Tom Bullington (KBR)
1379 | Piping - Drawings, Specification & Electronic Models | Mechanical | Piping - Drawings, Specification & Electronic Models | Design | Quality | Piping - Drawings, Specification & Electronic Models | Be clear and consistent in use / call out of Bottom of Pipe (B.O.P.) or centerline dimensions or elevations on all drawings. | Tom Bullington (KBR)
1380 | Piping - Drawings, Specification & Electronic Models | Mechanical | Piping - Drawings, Specification & Electronic Models | Design | Quality | Piping - Drawings, Specification & Electronic Models | Isometrics should be drawn for all piping, including elevation changes, direction changes, and expansion loops. Such ISO should be fully dimensioned with coordinates. | Tom Bullington (KBR)
1381 | Piping - Drawings, Specification & Electronic Models | Mechanical | Piping - Drawings, Specification & Electronic Models | Design | Quality | Piping - Drawings, Specification & Electronic Models | The number of line classes should be minimized. | Tom Bullington (KBR)
1382 | Piping - Drawings, Specification & Electronic Models | Mechanical | Piping - Drawings, Specification & Electronic Models | Design | Quality | Piping - Drawings, Specification & Electronic Models | Double check that all P&ID notes are incorporated into isometrics. | Tom Bullington (KBR)
1383 | Piping - Drawings, Specification & Electronic Models | Mechanical | Piping - Drawings, Specification & Electronic Models | Design | Quality | Piping - Drawings, Specification & Electronic Models | Model small bore (2" and under) as well as large bore in PDS to minimize rework. | Tom Bullington (KBR)
1384 | Piping - Drawings, Specification & Electronic Models | Mechanical | Piping - Drawings, Specification & Electronic Models | Design | Quality | Piping - Drawings, Specification & Electronic Models | Valve handle orientations should be shown on the ISO / orthographic drawings. | Tom Bullington (KBR)
1385 | Piping - Drawings, Specification & Electronic Models | Mechanical | Piping - Drawings, Specification & Electronic Models | Design | Quality | Piping - Drawings, Specification & Electronic Models | Mark field welds and field fit-up welds on Isometrics before they leave the engineer's office. Field Fit-up Welds must be provided with 3” to 6” of pipe for field fit purposes. | Tom Bullington (KBR)
1386 | Piping - Drawings, Specification & Electronic Models | Mechanical | Piping - Drawings, Specification & Electronic Models | Design | Quality | Piping - Drawings, Specification & Electronic Models | Design engineering should furnish routing schematics for cooling, seal and lube piping. | Tom Bullington (KBR)
1387 | Piping - Drawings, Specification & Electronic Models | Mechanical | Piping - Drawings, Specification & Electronic Models | Design | Quality | Piping - Drawings, Specification & Electronic Models | Do isometrics have Post Weld Heat Treatment callouts? | Tom Bullington (KBR)
1388 | Piping - Drawings, Specification & Electronic Models | Mechanical | Piping - Drawings, Specification & Electronic Models | Design | Quality | Piping - Drawings, Specification & Electronic Models | Do isometrics have Boiler coded work and limits callouts? | Tom Bullington (KBR)
1389 | Piping - Drawings, Specification & Electronic Models | Mechanical | Piping - Drawings, Specification & Electronic Models | Design | Quality | Piping - Drawings, Specification & Electronic Models | Do isometrics have NDE requirment callouts? | Tom Bullington (KBR)
1390 | Piping - Drawings, Specification & Electronic Models | Mechanical | Piping - Drawings, Specification & Electronic Models | Design | Quality | Piping - Drawings, Specification & Electronic Models | Do isometrics have Bi-metal, alloy and field weld callouts? | Tom Bullington (KBR)
1391 | Piping - Drawings, Specification & Electronic Models | Mechanical | Piping - Drawings, Specification & Electronic Models | Design | Quality | Piping - Drawings, Specification & Electronic Models | Do isometrics have gussets or special bracing callouts? | Tom Bullington (KBR)
1392 | Piping - Drawings, Specification & Electronic Models | Mechanical | Piping - Drawings, Specification & Electronic Models | Design | Quality | Piping - Drawings, Specification & Electronic Models | Do Isometrics have jacking bolt hole drilling callouts? | Tom Bullington (KBR)
1393 | Piping - Drawings, Specification & Electronic Models | Mechanical | Piping - Drawings, Specification & Electronic Models | Design | Quality | Piping - Drawings, Specification & Electronic Models | Do Isometrics have paint, coating and insulation requirement callouts? | Tom Bullington (KBR)
1394 | Piping - Drawings, Specification & Electronic Models | Mechanical | Piping - Drawings, Specification & Electronic Models | Design | Quality | Piping - Drawings, Specification & Electronic Models | Do Isometrics have cold spring requirements at specific locations callouts? | Tom Bullington (KBR)
1395 | Piping - Drawings, Specification & Electronic Models | Mechanical | Piping - Drawings, Specification & Electronic Models | Design | Quality | Piping - Drawings, Specification & Electronic Models | Do isometrics have stress analysis callouts? | Tom Bullington (KBR)
1396 | Piping - Drawings, Specification & Electronic Models | Mechanical | Piping - Drawings, Specification & Electronic Models | Design | Quality | Piping - Drawings, Specification & Electronic Models | Do isometrics show system, WBS and CWP numbers? | Tom Bullington (KBR)
1397 | Piping - Drawings, Specification & Electronic Models | Mechanical | Piping - Drawings, Specification & Electronic Models | Design | Quality | Piping - Drawings, Specification & Electronic Models | Do isometrics have test medium and test pressure callouts? | Tom Bullington (KBR)
1398 | Piping - Drawings, Specification & Electronic Models | Mechanical | Piping - Drawings, Specification & Electronic Models | Design | Quality | Piping - Drawings, Specification & Electronic Models | Do isometrics show operating pressures and termperature callouts? | Tom Bullington (KBR)
1399 | Piping - Drawings, Specification & Electronic Models | Mechanical | Piping - Drawings, Specification & Electronic Models | Design | Quality | Piping - Drawings, Specification & Electronic Models | Does line list include insulation requirements (thickness and type)? | Tom Bullington (KBR)
1400 | Piping - Drawings, Specification & Electronic Models | Mechanical | Piping - Drawings, Specification & Electronic Models | Design | Quality | Piping - Drawings, Specification & Electronic Models | Does line list include paint specification? | Tom Bullington (KBR)
1401 | Piping - Drawings, Specification & Electronic Models | Mechanical | Piping - Drawings, Specification & Electronic Models | Design | Quality | Piping - Drawings, Specification & Electronic Models | Does line list include size and number of steam & electric tracers | Tom Bullington (KBR)
1402 | Piping - Drawings, Specification & Electronic Models | Mechanical | Piping - Drawings, Specification & Electronic Models | Design | Quality | Piping - Drawings, Specification & Electronic Models | Does line list include turnover system reference | Tom Bullington (KBR)
1403 | Piping - Drawings, Specification & Electronic Models | Mechanical | Piping - Drawings, Specification & Electronic Models | Design | Quality | Piping - Drawings, Specification & Electronic Models | Does line list show test package references | Tom Bullington (KBR)
1404 | Piping - Drawings, Specification & Electronic Models | Mechanical | Piping - Drawings, Specification & Electronic Models | Design | Quality | Piping - Drawings, Specification & Electronic Models | Does line list show "To and From" references | Tom Bullington (KBR)
1405 | Piping - Drawings, Specification & Electronic Models | Mechanical | Piping - Drawings, Specification & Electronic Models | Design | Quality | Piping - Drawings, Specification & Electronic Models | Does line list show P&ID references? | Tom Bullington (KBR)
1406 | Piping - Drawings, Specification & Electronic Models | Mechanical | Piping - Drawings, Specification & Electronic Models | Design | Quality | Piping - Drawings, Specification & Electronic Models | Does line list show test pressure and medium? | Tom Bullington (KBR)
1407 | Piping - Drawings, Specification & Electronic Models | Mechanical | Piping - Drawings, Specification & Electronic Models | Design | Quality | Piping - Drawings, Specification & Electronic Models | Does line list provide seal water details for process equipment | Tom Bullington (KBR)
1408 | Piping - Fabrication | Mechanical | Piping - Fabrication | Design | Quality | Piping - Fabrication | Isometrics should be made for equipment trim and issued as early as possible (vessels, pumps, exchangers, etc.) | Tom Bullington (KBR)
1409 | Piping - Fabrication | Mechanical | Piping - Fabrication | Design | Quality | Piping - Fabrication | Consider pipe bending in lieu of fittings. Pipe bending will improve on shop fabrication delivery schedule time because of less welding and NDE inspection | Tom Bullington (KBR)
1410 | Piping - Fabrication | Mechanical | Piping - Fabrication | Design | Quality | Piping - Fabrication | Leave a field weld at the last flange on all rotating equipment on shop fabricated piping. (Shop fabricator should ship flange tacked to spool). | Tom Bullington (KBR)
1411 | Piping - Fabrication | Mechanical | Piping - Fabrication | Design | Quality | Piping - Fabrication | Consider maximizing shop fabrication regardless of size by remote vendor shop including repetitive assemblies (steam trap assemblies, utility stations, steam trace manifolds, sample coolers, etc.) | Tom Bullington (KBR)
1412 | Piping - Fabrication | Mechanical | Piping - Fabrication | Design | Quality | Piping - Fabrication | Check straight run pipe for the pipe racks, including steam tracing, to see if it is practical to fabricate into lengths up to 80 feet. Sandblast prime and topcoat (if required) and install with the pipe rack steel as the tiers of the rack are installed. Purchase double random lengths where possible. | Tom Bullington (KBR)
1413 | Piping - Fabrication | Mechanical | Piping - Fabrication | Design | Quality | Piping - Fabrication | Fabricators should be selected by reason of their proven ability to meet required schedules and fabrication accuracy rather than solely on a price basis. | Tom Bullington (KBR)
1414 | Piping - Fabrication | Mechanical | Piping - Fabrication | Design | Quality | Piping - Fabrication | Maximize shop fabrication of instrument bridles and other piping assembles. | Tom Bullington (KBR)
1415 | Piping - Insulation & Coatings | Mechanical | Piping - Insulation & Coatings | Design | Quality | Piping - Insulation & Coatings | Pipe clearances between pipes, structural members, equipment, etc., should be sufficient to avoid field trimming of insulation (Including shoes on steam traced lines). | Tom Bullington (KBR)
1416 | Piping - Insulation & Coatings | Mechanical | Piping - Insulation & Coatings | Design | Quality | Piping - Insulation & Coatings | Isometrics and orthographic drawings should clearly denote insulation limits for personnel protection, steam tracing and acoustical and insulation spec break points. | Tom Bullington (KBR)
1417 | Piping - Insulation & Coatings | Mechanical | Piping - Insulation & Coatings | Design | Quality | Piping - Insulation & Coatings | Vessel Trim Drawings for level gauges and switches, etc., on towers should have vertical and horizontal dimensions, particularly in its interface with insulation and not be classified as "field run." | Tom Bullington (KBR)
1418 | Piping - Insulation & Coatings | Mechanical | Piping - Insulation & Coatings | Design | Quality | Piping - Insulation & Coatings | Prime and top coat shop fabricated pipe. Use paints such as aluminum oxide on field weld preparations. Tape field-welds to avoid painting the weld heat area. | Tom Bullington (KBR)
1419 | Piping - Insulation & Coatings | Mechanical | Piping - Insulation & Coatings | Design | Quality | Piping - Insulation & Coatings | Specify pre-insulated tubing in lieu of hand insulated piping for steam tracing supply and return lines, where practical. | Tom Bullington (KBR)
1420 | Piping - Insulation & Coatings | Mechanical | Piping - Insulation & Coatings | Design | Quality | Piping - Insulation & Coatings | Maximize pre-painting and use of maximum of two-coat paint applications and include in pipe fabricator purchase order. | Tom Bullington (KBR)
1421 | Piping - Marking & Identification | Mechanical | Piping - Marking & Identification | Design | Quality | Piping - Marking & Identification | Vendor supplied piping should be shown on isometrics and orthographic drawings and identified according to vendor piece marks. | Tom Bullington (KBR)
1422 | Piping - Marking & Identification | Mechanical | Piping - Marking & Identification | Design | Quality | Piping - Marking & Identification | Spool piece numbers will be shown by the engineers with a method differentiating between offsite shop and field spool fabrications. | Tom Bullington (KBR)
1423 | Piping - Marking & Identification | Mechanical | Piping - Marking & Identification | Design | Quality | Piping - Marking & Identification | Have line ID tagged in large letters on beams supporting all pipe headers (size, number, and class). Incorporate into BID instructions. | Tom Bullington (KBR)
1424 | Piping - Marking & Identification | Mechanical | Piping - Marking & Identification | Design | Quality | Piping - Marking & Identification | System or area color coding (circumference stripping) should be used for shop fabricated spools and should be shown on each isometric drawing. | Tom Bullington (KBR)
1425 | Piping - Materials | Mechanical | Piping - Materials | Design | Quality | Piping - Materials | Utilize maximum-minimum system for small bore piping materials, bolts and gaskets. | Tom Bullington (KBR)
1426 | Piping - Materials | Mechanical | Piping - Materials | Design | Quality | Piping - Materials | Use field engineers for material take-off checks in the home office. | Tom Bullington (KBR)
1427 | Piping - Materials | Mechanical | Piping - Materials | Design | Quality | Piping - Materials | If any coded work is required on the project, the piping bulks must be purchased with "mill test" papers. | Tom Bullington (KBR)
1428 | Piping - Materials | Mechanical | Piping - Materials | Design | Quality | Piping - Materials | A piping specialty list should be maintained for tagged items such as de-superheaters, ejectors, in-line strainers and any other tagged piping items. | Tom Bullington (KBR)
1429 | Piping - Materials | Mechanical | Piping - Materials | Design | Quality | Piping - Materials | Preliminary Material Take-offs (MTOs) should include non-engineered pipe supports (shoes, guides, anchors, etc.) for early purchase and fabrication. | Tom Bullington (KBR)
1430 | Piping - Materials | Mechanical | Piping - Materials | Design | Quality | Piping - Materials | Run cost analysis on using all stainless steel for lube-oil systems. Clearly define cleaning procedure. Avoid bottom connections. | Tom Bullington (KBR)
1431 | Piping - Materials | Mechanical | Piping - Materials | Design | Quality | Piping - Materials | Ensure installation manuals and procedures are available for nonmetallic pipe (i.e. GRE, HDPE). Set-up supplier interface. | Tom Bullington (KBR)
1432 | Piping - Materials | Mechanical | Piping - Materials | Design | Quality | Piping - Materials | Design and order valves early. Evaluate the risks of ordering valves based on P&IDs prior to rev. 0 against potential schedule delays. | Tom Bullington (KBR)
1433 | Piping - Materials | Mechanical | Piping - Materials | Design | Quality | Piping - Materials | Valves with welding ends and soft seats or internals that can be damaged or destroyed by field welding should be provided with 6-inch nipples attached by the vendor or develop other protection plan. | Tom Bullington (KBR)
1434 | Piping - Materials | Mechanical | Piping - Materials | Design | Quality | Piping - Materials | Carefully check for correct valve trim, bolts, packing, gaskets and flange facing specifications prior to ordering valves. | Tom Bullington (KBR)
1435 | Piping - Materials | Mechanical | Piping - Materials | Design | Quality | Piping - Materials | Ensure valve manufacturers provide care and protection procedures for gland packing, soft seats, etc. | Tom Bullington (KBR)
1436 | Piping - Materials | Mechanical | Piping - Materials | Design | Quality | Piping - Materials | Engineering to identify need for and order temporary strainers. | Tom Bullington (KBR)
1437 | Piping - Materials | Mechanical | Piping - Materials | Design | Quality | Piping - Materials | Provide specifications for preventative maintenance and storage requirements of specialty items. | Tom Bullington (KBR)
1438 | Piping - Piping Tie-Ins | Mechanical | Piping - Piping Tie-Ins | Design | Quality | Piping - Piping Tie-Ins | Maintain operability of a system after a tie-in has been made and before the start-up of the new system. Consider providing a block valve or spec blind with weld neck flange to isolate the new system from the existing system. | Tom Bullington (KBR)
1439 | Piping - Piping Tie-Ins | Mechanical | Piping - Piping Tie-Ins | Design | Quality | Piping - Piping Tie-Ins | Identify tie-in procedures (i.e., unit shutdown, system shutdown and hot tap) early in the design phase. (Test pressure and test methods, test medium and items to be removed for pressure test, Tie-in method, welded, flanges and blind and or isolation rquirement and ideinfication numger | Tom Bullington (KBR)
1440 | Piping - Piping Tie-Ins | Mechanical | Piping - Piping Tie-Ins | Design | Quality | Piping - Piping Tie-Ins | Identify and prioritize tie-in material on purchase orders. | Tom Bullington (KBR)
1441 | Piping - Piping Tie-Ins | Mechanical | Piping - Piping Tie-Ins | Design | Quality | Piping - Piping Tie-Ins | Specify tie-in NDE requirements where tie-in of pipe to operating plant makes hydrotesting impractical or impossible. consider 100% N.D.E. of welds | Tom Bullington (KBR)
1442 | Piping - Piping Tie-Ins | Mechanical | Piping - Piping Tie-Ins | Design | Quality | Piping - Piping Tie-Ins | Verify and field check quality of piping to be tied into before final design and fabrication of tie-in spools for integrity, ability to isolate, material spec. / thickness and interference’s. Identify all tie-in locations with tie-in ID Tags and develop a detailed tie-in listing. | Tom Bullington (KBR)
1443 | Piping - Scheduling | Mechanical | Piping - Scheduling | Design | Schedule Performance | Piping - Scheduling | Provide early issue of types of metals / alloys to be utilized and Wall Thickness Schedules. | Tom Bullington (KBR)
1444 | Piping - Scheduling | Mechanical | Piping - Scheduling | Design | Schedule Performance | Piping - Scheduling | Engineering to provide isometric issue forecast curve, with input from Construction. | Tom Bullington (KBR)
1445 | Piping - Scheduling | Mechanical | Piping - Scheduling | Design | Schedule Performance | Piping - Scheduling | Finalize designs and release for construction of all larger lines early in the program. Smaller pipes can follow in agreed staged sequences. | Tom Bullington (KBR)
1446 | Piping - Scheduling | Mechanical | Piping - Scheduling | Design | Schedule Performance | Piping - Scheduling | Encourage preparation and early release of separate pipe hanger and support drawings so that specialist crews can install supports ahead of erection crews. | Tom Bullington (KBR)
1447 | Piping - Scheduling | Mechanical | Piping - Scheduling | Design | Schedule Performance | Piping - Scheduling | Design the deeper underground piping systems first. | Tom Bullington (KBR)
1448 | Piping - Scheduling | Mechanical | Piping - Scheduling | Design | Schedule Performance | Piping - Scheduling | Priorities for off-site shop fabricated piping should have input from Construction. | Tom Bullington (KBR)
1449 | Piping - Scheduling | Mechanical | Piping - Scheduling | Design | Schedule Performance | Piping - Scheduling | Commit upon firm sequences for spool fabrication and delivery with the fabricator and maintain procedures to require them to follow the program even if this means that they cannot do all like items together or work in other ways to sustain shop efficiency at the expense of field inefficiency. When necessary a special schedule / expeditor can be designated for the pipe fabricator's shop. Provide for routine inspection visits of the fabricator's shop. | Tom Bullington (KBR)
1450 | Piping - Scheduling | Mechanical | Piping - Scheduling | Design | Schedule Performance | Piping - Scheduling | Identify for early fabrication, any spools, which should be lowered into basements, tunnels or other areas, prior to construction of roofs. These spools can be initially placed on the floors for later erection. | Tom Bullington (KBR)
1451 | Piping - Scheduling | Mechanical | Piping - Scheduling | Design | Schedule Performance | Piping - Scheduling | Review major pipe runs and establish sequences for dropping lines into position in a program coordinated with erection of structural members. | Tom Bullington (KBR)
1452 | Piping - Scheduling | Mechanical | Piping - Scheduling | Design | Schedule Performance | Piping - Scheduling | Design roof and floor drains early. | Tom Bullington (KBR)
1453 | Piping - Supports & Restraints | Mechanical | Piping - Supports & Restraints | Design | Quality | Piping - Supports & Restraints | All engineered supports and hangers should be located with coordinates, elevations and clearly identified by tag and / or catalogue number on isometrics and / or orthographic drawings. | Tom Bullington (KBR)
1454 | Piping - Supports & Restraints | Mechanical | Piping - Supports & Restraints | Design | Quality | Piping - Supports & Restraints | Check spring hanger, snubber and strut locations for interference with the structure and all rod-out connections. | Tom Bullington (KBR)
1455 | Piping - Supports & Restraints | Mechanical | Piping - Supports & Restraints | Design | Quality | Piping - Supports & Restraints | Spring hanger scales should be visible from a platform or ladder whenever possible. | Tom Bullington (KBR)
1456 | Piping - Supports & Restraints | Mechanical | Piping - Supports & Restraints | Design | Quality | Piping - Supports & Restraints | Minimize use of engineered supports and spring hangers. Use adjustable hanger supports and restraints wherever possible. | Tom Bullington (KBR)
1457 | Piping - Supports & Restraints | Mechanical | Piping - Supports & Restraints | Design | Quality | Piping - Supports & Restraints | Don't use galvanized shoes or clamps on SS lines at high temperatures. | Tom Bullington (KBR)
1458 | Piping - Supports & Restraints | Mechanical | Piping - Supports & Restraints | Design | Quality | Piping - Supports & Restraints | Consider use of mechanical fitted pipe shoes. | Tom Bullington (KBR)
1459 | Piping - Supports & Restraints | Mechanical | Piping - Supports & Restraints | Design | Quality | Piping - Supports & Restraints | Piping shoes, trunnions and dummy legs should be installed on shop fabricated spools by the fabricator and should have slots for insulation banding, if required. | Tom Bullington (KBR)
1460 | Piping - Supports & Restraints | Mechanical | Piping - Supports & Restraints | Design | Quality | Piping - Supports & Restraints | Base ells and other pipe support to paving shall be adjustable. | Tom Bullington (KBR)
1461 | Piping - Supports & Restraints | Mechanical | Piping - Supports & Restraints | Design | Quality | Piping - Supports & Restraints | Particular attention should be taken in detailing weld symbols on hanger details. Show necessary welds that are accessible and proper size for material being welded. | Tom Bullington (KBR)
1462 | Piping - Supports & Restraints | Mechanical | Piping - Supports & Restraints | Design | Quality | Piping - Supports & Restraints | Hanger components that do not require field assembly welding and are difficult to paint after installation should be shop painted with the appropriate paint system. This is particularly important for such items as snubbers, spring cans or struts. | Tom Bullington (KBR)
1463 | Piping - Supports & Restraints | Mechanical | Piping - Supports & Restraints | Design | Quality | Piping - Supports & Restraints | Standardize components used in hanger fabrication. | Tom Bullington (KBR)
1464 | Piping - Supports & Restraints | Mechanical | Piping - Supports & Restraints | Design | Quality | Piping - Supports & Restraints | Hydraulic snubbers must be installed with the oil reservoir plug on top for maintenance checking. | Tom Bullington (KBR)
1465 | Piping - Supports & Restraints | Mechanical | Piping - Supports & Restraints | Design | Quality | Piping - Supports & Restraints | Permanent hangers and supports should be designed and fabricated early. These and all associated materials should be delivered prior to arrival of pipe spools. Encourage preparation and early release of separate pipe hanger and support drawings so that specialist crews can install supports ahead of erection crews. | Tom Bullington (KBR)
1466 | Piping - Supports & Restraints | Mechanical | Piping - Supports & Restraints | Design | Quality | Piping - Supports & Restraints | Don't use base spring cans where large horizontal movements are anticipated. | Tom Bullington (KBR)
1467 | Piping - Supports & Restraints | Mechanical | Piping - Supports & Restraints | Design | Quality | Piping - Supports & Restraints | Avoid using tall "toothpick" type pipe supports, especially in seismic or high / gusty wind areas. | Tom Bullington (KBR)
1468 | Piping - Testing & Cleaning | Mechanical | Piping - Testing & Cleaning | Design | Quality | Piping - Testing & Cleaning | Establish clear parameters on testing requirements for tie-in valves or other tight shut-off valves. Specify leakage rate requirements and have valves tested by vendor prior to shipment. | Tom Bullington (KBR)
1469 | Piping - Testing & Cleaning | Mechanical | Piping - Testing & Cleaning | Design | Quality | Piping - Testing & Cleaning | Agree early to procedures and mark drawings in the design stage on method to test flare and other large lines. Verify structures are designed for hydrotest weights in vapor lines | Tom Bullington (KBR)
1470 | Piping - Testing & Cleaning | Mechanical | Piping - Testing & Cleaning | Design | Quality | Piping - Testing & Cleaning | Where chemical cleaning is required, design piping accordingly with adequate connections, drains, break out flanges to facilitate full circulation, draining and drying | Tom Bullington (KBR)
1471 | Piping - Testing & Cleaning | Mechanical | Piping - Testing & Cleaning | Design | Quality | Piping - Testing & Cleaning | Isometrics for compressor suction piping or other systems requiring chemical cleaning should have specific notes, which require removal of any internal protective coatings such as "black lacquer" in the SHOP. | Tom Bullington (KBR)
1472 | Piping - Testing & Cleaning | Mechanical | Piping - Testing & Cleaning | Design | Quality | Piping - Testing & Cleaning | Engineering should provide specifications and criteria for NDE requirements (RT, PT, UT, etc.) with construction and [Client] input. | Tom Bullington (KBR)
1473 | Piping - Testing & Cleaning | Mechanical | Piping - Testing & Cleaning | Design | Quality | Piping - Testing & Cleaning | Provide early definition of chemical cleaning requirements, i.e., specifications to be used, valves required and lines. | Tom Bullington (KBR)
1474 | Piping - Testing & Cleaning | Mechanical | Piping - Testing & Cleaning | Design | Quality | Piping - Testing & Cleaning | The Design Engineer along with Construction input should identify testing and cleaning systems by marking up P&IDs. | Tom Bullington (KBR)
1475 | Piping - Testing & Cleaning | Mechanical | Piping - Testing & Cleaning | Design | Quality | Piping - Testing & Cleaning | The engineer should specify which services can be service tested (cooling water, drinking water, instrument air, plant air, etc.) in lieu of pressure testing. Should be able to service test all category “D” piping. | Tom Bullington (KBR)
1476 | Piping - Testing & Cleaning | Mechanical | Piping - Testing & Cleaning | Design | Quality | Piping - Testing & Cleaning | Consider steam testing of piping designed for steam-out conditions in lieu of hydrostatic testing. | Tom Bullington (KBR)
1477 | Piping - Turnover | Mechanical | Piping - Turnover | Design | Quality | Piping - Turnover | Develop a set of System Boundary P&IDs, which are color-coded by turnover systems. Incorporate databases with a field for system identification early in design that includes line lists, equipment lists and instrument indexes etc. | Tom Bullington (KBR)
1478 | Piping - Turnover | Mechanical | Piping - Turnover | Design | Quality | Piping - Turnover | Enter into discussions with the start-up and commissioning group early in the program so that the required final systems sequences can be worked backward into the initial planning. | Tom Bullington (KBR)
1479 | Piping - Turnover | Mechanical | Piping - Turnover | Design | Quality | Piping - Turnover | Provide [Client] a master set of piping specifications and welding procedures at end of project. They should include all data reports and quality documentation. | Tom Bullington (KBR)
1480 | Piping - Underground | Mechanical | Piping - Underground | Design | Quality | Piping - Underground | Field construction engineering to keep accurate “As Built” dimensions and coordinates of installed underground piping and components. | Tom Bullington (KBR)
1481 | Piping - Underground | Mechanical | Piping - Underground | Design | Quality | Piping - Underground | Where feasible underground piping should be located so that multiple installation can be achieved with a single excavation particularly at road crossings. | Tom Bullington (KBR)
1482 | Piping - Underground | Mechanical | Piping - Underground | Design | Quality | Piping - Underground | Specify adjustable drains and cleanouts, when possible. | Tom Bullington (KBR)
1483 | Piping - Underground | Mechanical | Piping - Underground | Design | Quality | Piping - Underground | Underground piping and electrical conduit should each be run at consistent elevations in zones, whenever possible. | Tom Bullington (KBR)
1484 | Piping - Underground | Mechanical | Piping - Underground | Design | Quality | Piping - Underground | Provide all drain piping with adequate clean-out access. (Assume all drainpipes will plug at some point in time.) | Tom Bullington (KBR)
1485 | Piping - Underground | Mechanical | Piping - Underground | Design | Quality | Piping - Underground | Engineering design utilize specifications of HDPE, fiberglass and plastic piping weight advantages, ease of installation, etc. | Tom Bullington (KBR)
1486 | Piping - Welding | Mechanical | Piping - Welding | Design | Quality | Piping - Welding | Ensure welding specifications allow for use of automatic / semi-automatic welding on large bore piping. | Tom Bullington (KBR)
1487 | Piping - Welding | Mechanical | Piping - Welding | Design | Quality | Piping - Welding | Take steps to minimize the number of required welding procedures and welder qualification procedures. | Tom Bullington (KBR)
1488 | Piping - Welding | Mechanical | Piping - Welding | Design | Quality | Piping - Welding | Consider the use of orbital welding and / or LOCKRING joints to reduce field welding. | Tom Bullington (KBR)
1489 | Piping - Welding | Mechanical | Piping - Welding | Design | Quality | Piping - Welding | Review supplier's Welding Procedure Specification (WPS) for conformance to applicable code and [Client] requirements. | Tom Bullington (KBR)
1490 | Piping - Welding | Mechanical | Piping - Welding | Design | Quality | Piping - Welding | Verify pipe clearance between pipes, supports, etc. will facilitate the use of orbital automatic welding equipment on heavy wall pipe. | Tom Bullington (KBR)
1491 | Piping - Welding | Mechanical | Piping - Welding | Design | Quality | Piping - Welding | Use flux cored arc welding on all heavy wall carbon steel piping. | Tom Bullington (KBR)
1492 | Piping - Welding | Mechanical | Piping - Welding | Design | Quality | Piping - Welding | Engineering should closely review the welding and non-destructive examination requirements that are imposed on supplier components for compatibility and feasibility with project's welding and NDE Standards. Suppliers should be given explicit instructions regarding tests, documentation and approval. Requirements should refer to specific sections of applicable codes. Supplier welding and NDE procedures should be reviewed by Engineering for Home Office procured components and by the Construction/ Maintenance Function for field procured components. | Tom Bullington (KBR)
1493 | Plot Plan & Equipment Arrangement - Civil & Concrete | Civil | Plot Plan & Equipment Arrangement - Civil & Concrete | Design | Quality | Plot Plan & Equipment Arrangement - Civil & Concrete | Group equipment so that mass excavation can be minimized and earthwork can be balanced. | Tom Bullington (KBR)
1494 | Plot Plan & Equipment Arrangement - Civil & Concrete | Civil | Plot Plan & Equipment Arrangement - Civil & Concrete | Design | Quality | Plot Plan & Equipment Arrangement - Civil & Concrete | Group equipment so that large common foundation mats can be used, whenever practical. | Tom Bullington (KBR)
1495 | Plot Plan & Equipment Arrangement - Civil & Concrete | Civil | Plot Plan & Equipment Arrangement - Civil & Concrete | Design | Quality | Plot Plan & Equipment Arrangement - Civil & Concrete | Raise and slope plot elevation to facilitate drainage during construction and permanent facility design. Consider use of temporary ditching. | Tom Bullington (KBR)
1496 | Plot Plan & Equipment Arrangement - Equipment Accessibility | Other | Plot Plan & Equipment Arrangement - Equipment Accessibility | Design | Quality | Plot Plan & Equipment Arrangement - Equipment Accessibility | Consider where emergency stop stations should be located throughout the production area. | Tom Bullington (KBR)
1497 | Plot Plan & Equipment Arrangement - Equipment Accessibility | Other | Plot Plan & Equipment Arrangement - Equipment Accessibility | Design | Quality | Plot Plan & Equipment Arrangement - Equipment Accessibility | Improve oil sight gauges for easy operator access. | Tom Bullington (KBR)
1498 | Plot Plan & Equipment Arrangement - Equipment Accessibility | Other | Plot Plan & Equipment Arrangement - Equipment Accessibility | Design | Quality | Plot Plan & Equipment Arrangement - Equipment Accessibility | Design surge stations into multi-process production lines to reduce sensitivity to exactly matching production rates. | Tom Bullington (KBR)
1499 | Plot Plan & Equipment Arrangement - Equipment Accessibility | Other | Plot Plan & Equipment Arrangement - Equipment Accessibility | Design | Quality | Plot Plan & Equipment Arrangement - Equipment Accessibility | Provide interconnecting platform between equipment. | Tom Bullington (KBR)
1500 | Plot Plan & Equipment Arrangement - Equipment Accessibility | Other | Plot Plan & Equipment Arrangement - Equipment Accessibility | Design | Quality | Plot Plan & Equipment Arrangement - Equipment Accessibility | Allow space for piping and instrumentation next to equipment. | Tom Bullington (KBR)
1501 | Plot Plan & Equipment Arrangement - Equipment Accessibility | Other | Plot Plan & Equipment Arrangement - Equipment Accessibility | Design | Quality | Plot Plan & Equipment Arrangement - Equipment Accessibility | Provide platforms on equipment to facilitate routine maintenance requirements. | Tom Bullington (KBR)
1502 | Plot Plan & Equipment Arrangement - Equipment Accessibility | Other | Plot Plan & Equipment Arrangement - Equipment Accessibility | Design | Quality | Plot Plan & Equipment Arrangement - Equipment Accessibility | Consider maintenance requirements when designing permanent walkways, ladders, stairways, platforms, and elevators. | Tom Bullington (KBR)
1503 | Plot Plan & Equipment Arrangement - Equipment Accessibility | Other | Plot Plan & Equipment Arrangement - Equipment Accessibility | Design | Quality | Plot Plan & Equipment Arrangement - Equipment Accessibility | Develop plot plan and equipment arrangement to allow adequate access for construction and maintenance. Provide wide roads and gates to accommodate cranes. Provide crane access to heavingy | Tom Bullington (KBR)
1504 | Plot Plan & Equipment Arrangement - Equipment Accessibility | Other | Plot Plan & Equipment Arrangement - Equipment Accessibility | Design | Quality | Plot Plan & Equipment Arrangement - Equipment Accessibility | rovide wide roads and gates to accommodate cranes. Provide crane access to heavy equipment. | Tom Bullington (KBR)
1505 | Plot Plan & Equipment Arrangement - Equipment Accessibility | Other | Plot Plan & Equipment Arrangement - Equipment Accessibility | Design | Quality | Plot Plan & Equipment Arrangement - Equipment Accessibility | · Provide wider than needed pipe ways and alleyways to accommodate such items as protruding valve stems, manifolds, and fire hoses. Avoid locating pumps or other equipment under pipe ways or restricted access. | Tom Bullington (KBR)
1506 | Plot Plan & Equipment Arrangement - Equipment Accessibility | Other | Plot Plan & Equipment Arrangement - Equipment Accessibility | Design | Quality | Plot Plan & Equipment Arrangement - Equipment Accessibility | Verify that plot plan/equipment arrangement and construction sequencing will not close haul routes for heavy equipment due to height, width, length and weight restrictions. Orient equipment to accommodate haul routes. | Tom Bullington (KBR)
1507 | Plot Plan & Equipment Arrangement - Equipment Accessibility | Other | Plot Plan & Equipment Arrangement - Equipment Accessibility | Design | Quality | Plot Plan & Equipment Arrangement - Equipment Accessibility | Provide stair (not ladder) access to all areas requiring routine maintenance to facilitate transport of tools and supplies required for maintenance. Provide access on as many sides of equipment as practical. | Tom Bullington (KBR)
1508 | Plot Plan & Equipment Arrangement - Equipment Accessibility | Other | Plot Plan & Equipment Arrangement - Equipment Accessibility | Design | Quality | Plot Plan & Equipment Arrangement - Equipment Accessibility | Review proposed layouts with operations personnel to provide most efficient arrangement. | Tom Bullington (KBR)
1509 | Plot Plan & Equipment Arrangement - Equipment Accessibility | Other | Plot Plan & Equipment Arrangement - Equipment Accessibility | Design | Quality | Plot Plan & Equipment Arrangement - Equipment Accessibility | Determine best location of controls to match operator areas and provide view of equipment. | Tom Bullington (KBR)
1510 | Plot Plan & Equipment Arrangement - Equipment Accessibility | Other | Plot Plan & Equipment Arrangement - Equipment Accessibility | Design | Quality | Plot Plan & Equipment Arrangement - Equipment Accessibility | · Arrange equipment as close to the flow logic as possible by grouping equipment by process system. | Tom Bullington (KBR)
1511 | Plot Plan & Equipment Arrangement - Equipment Accessibility | Other | Plot Plan & Equipment Arrangement - Equipment Accessibility | Design | Quality | Plot Plan & Equipment Arrangement - Equipment Accessibility | Review access to critical equipment for removal and replacement, especially for large items that cannot be "manhandled". Consider removable roof panels, crane lifts, elevators, and removable wall sections. Provide drop areas at grade for motors and other equipment removed for maintenance. Consider use of installed spare equipment. | Tom Bullington (KBR)
1512 | Plot Plan & Equipment Arrangement - Equipment Accessibility | Other | Plot Plan & Equipment Arrangement - Equipment Accessibility | Design | Quality | Plot Plan & Equipment Arrangement - Equipment Accessibility | Consider size of existing maintenance equipment when establishing equipment heights and locating equipment above grade. Establish aisle ways large enough to accommodate mini-cranes. | Tom Bullington (KBR)
1513 | Plot Plan & Equipment Arrangement - Equipment Accessibility | Other | Plot Plan & Equipment Arrangement - Equipment Accessibility | Design | Quality | Plot Plan & Equipment Arrangement - Equipment Accessibility | Allow space for functional expansions of facility, which will also minimize demolition requirements. | Tom Bullington (KBR)
1514 | Plot Plan & Equipment Arrangement - Equipment Accessibility | Other | Plot Plan & Equipment Arrangement - Equipment Accessibility | Design | Quality | Plot Plan & Equipment Arrangement - Equipment Accessibility | Have rigging specialist review plot plan / equipment arrangement to ensure heavy lifts can be made. | Tom Bullington (KBR)
1515 | Plot Plan & Equipment Arrangement - Equipment Accessibility | Other | Plot Plan & Equipment Arrangement - Equipment Accessibility | Design | Quality | Plot Plan & Equipment Arrangement - Equipment Accessibility | Consider maximum use of large construction equipment to set several vessels from one location by moving vessel locations to stay within the chart limits of the crane. | Tom Bullington (KBR)
1516 | Plot Plan & Equipment Arrangement - Equipment Accessibility | Other | Plot Plan & Equipment Arrangement - Equipment Accessibility | Design | Quality | Plot Plan & Equipment Arrangement - Equipment Accessibility | Provide adequate space for shower, locker, change and restroom facilities for operations personnel, if required. | Tom Bullington (KBR)
1517 | Plot Plan & Equipment Arrangement - Equipment Accessibility | Other | Plot Plan & Equipment Arrangement - Equipment Accessibility | Design | Quality | Plot Plan & Equipment Arrangement - Equipment Accessibility | Arrange equipment to support operations as follows: | Tom Bullington (KBR)
1518 | Plot Plan & Equipment Arrangement - General | Other | Plot Plan & Equipment Arrangement - General | Design | Quality | Plot Plan & Equipment Arrangement - General | Decide early whether or not to modularize either partial or full scale. | Tom Bullington (KBR)
1519 | Plot Plan & Equipment Arrangement - General | Other | Plot Plan & Equipment Arrangement - General | Design | Quality | Plot Plan & Equipment Arrangement - General | Decide on final plot plan / equipment arrangement early and hold to plan. When possible, obtain supplier input during development. | Tom Bullington (KBR)
1520 | Plot Plan & Equipment Arrangement - Pipe Racks | Other | Plot Plan & Equipment Arrangement - Pipe Racks | Design | Quality | Plot Plan & Equipment Arrangement - Pipe Racks | Leave end of pipe racks open for stuffing. Design pipe in sequence so it can be installed in conjunction with pipe bridge construction. | Tom Bullington (KBR)
1521 | Plot Plan & Equipment Arrangement - Pipe Racks | Other | Plot Plan & Equipment Arrangement - Pipe Racks | Design | Quality | Plot Plan & Equipment Arrangement - Pipe Racks | Arrange equipment to reduce length of pipe racks. | Tom Bullington (KBR)
1522 | Plot Plan & Equipment Arrangement - Safety | Other | Plot Plan & Equipment Arrangement - Safety | Design | Safety | Plot Plan & Equipment Arrangement - Safety | Maximize ground level construction when possible | Tom Bullington (KBR)
1523 | Plot Plan & Equipment Arrangement - Safety | Other | Plot Plan & Equipment Arrangement - Safety | Design | Safety | Plot Plan & Equipment Arrangement - Safety | Provide direct access ways / aisles to minimize tripping / congestion hazards and provide escape routes during emergencies | Tom Bullington (KBR)
1524 | Plot Plan & Equipment Arrangement - Safety | Other | Plot Plan & Equipment Arrangement - Safety | Design | Safety | Plot Plan & Equipment Arrangement - Safety | Locate new equipment away from existing equipment to minimize use of "Hot Work" permits | Tom Bullington (KBR)
1525 | Plot Plan & Equipment Arrangement - Safety | Other | Plot Plan & Equipment Arrangement - Safety | Design | Safety | Plot Plan & Equipment Arrangement - Safety | Separate new foundations from existing units to minimize requirements for sheet pilling or shoring | Tom Bullington (KBR)
1526 | Plot Plan & Equipment Arrangement - Safety | Other | Plot Plan & Equipment Arrangement - Safety | Design | Safety | Plot Plan & Equipment Arrangement - Safety | Consolidate or limit hearing protection areas | Tom Bullington (KBR)
1527 | Plot Plan & Equipment Arrangement - Safety | Other | Plot Plan & Equipment Arrangement - Safety | Design | Safety | Plot Plan & Equipment Arrangement - Safety | Provide locations for safety showers and eyewashes | Tom Bullington (KBR)
1528 | Plot Plan & Equipment Arrangement - Safety | Other | Plot Plan & Equipment Arrangement - Safety | Design | Safety | Plot Plan & Equipment Arrangement - Safety | Locate hazardous materials yellow line area compactly and continuously near edge of plant. | Tom Bullington (KBR)
1529 | Plot Plan & Equipment Arrangement - Safety | Other | Plot Plan & Equipment Arrangement - Safety | Design | Safety | Plot Plan & Equipment Arrangement - Safety | Locate equipment so that it is not shielded from fire monitors and is accessible for fire fighting equipment | Tom Bullington (KBR)
1530 | Plot Plan & Equipment Arrangement - Safety | Other | Plot Plan & Equipment Arrangement - Safety | Design | Safety | Plot Plan & Equipment Arrangement - Safety | Provide visitor access separate from operations | Tom Bullington (KBR)
1531 | Plot Plan & Equipment Arrangement - Safety | Other | Plot Plan & Equipment Arrangement - Safety | Design | Safety | Plot Plan & Equipment Arrangement - Safety | Locate equipment to minimize fireproofing requirements | Tom Bullington (KBR)
1532 | Plot Plan & Equipment Arrangement - Scheduling | Other | Plot Plan & Equipment Arrangement - Scheduling | Design | Schedule Performance | Plot Plan & Equipment Arrangement - Scheduling | Arrange equipment to facilitate construction sequencing. | Tom Bullington (KBR)
1533 | Plot Plan & Equipment Arrangement - Scheduling | Other | Plot Plan & Equipment Arrangement - Scheduling | Design | Schedule Performance | Plot Plan & Equipment Arrangement - Scheduling | Ensure that plot plan and equipment arrangement contingency allows for late delivery of large equipment so that other work can proceed and late arrival equipment can be set when delivered. Arrange plot plan and equipment consistent with module / skid delivery with full or partial modular program. | Tom Bullington (KBR)
1534 | Plot Plan & Equipment Arrangement - Temporary Facilities | Other | Plot Plan & Equipment Arrangement - Temporary Facilities | Design | Quality | Plot Plan & Equipment Arrangement - Temporary Facilities | Provide layout of buildings and equipment to accommodate prefabrication areas adjacent to work areas and / or performed in the same general area. | Tom Bullington (KBR)
1535 | Plot Plan & Equipment Arrangement - Temporary Facilities | Other | Plot Plan & Equipment Arrangement - Temporary Facilities | Design | Quality | Plot Plan & Equipment Arrangement - Temporary Facilities | Develop plot plan to accommodate temporary construction facilities (lay down area, parking lots, fabrication shops and construction offices) as well as permanent support facilities (warehouses, roads, parking lots and maintenance shops). | Tom Bullington (KBR)
1536 | Plot Plan & Equipment Arrangement - Temporary Facilities | Other | Plot Plan & Equipment Arrangement - Temporary Facilities | Design | Quality | Plot Plan & Equipment Arrangement - Temporary Facilities | Provide staging space for items pre-assembled at site such as stacks and platforms | Tom Bullington (KBR)
1537 | Plot Plan & Equipment Arrangement - Utilities | Other | Plot Plan & Equipment Arrangement - Utilities | Design | Quality | Plot Plan & Equipment Arrangement - Utilities | Locate waste sumps near the edge of plot. | Tom Bullington (KBR)
1538 | Plot Plan & Equipment Arrangement - Utilities | Other | Plot Plan & Equipment Arrangement - Utilities | Design | Quality | Plot Plan & Equipment Arrangement - Utilities | Locate underground utility corridors so that underground work does not affect the construction of deep foundations. | Tom Bullington (KBR)
1539 | Plot Plan & Equipment Arrangement - Utilities | Other | Plot Plan & Equipment Arrangement - Utilities | Design | Quality | Plot Plan & Equipment Arrangement - Utilities | Group electrical equipment in the least hazardous areas. Reduce hazard rating of equipment and enclosures. | Tom Bullington (KBR)
1540 | Plot Plan & Equipment Arrangement - Utilities | Other | Plot Plan & Equipment Arrangement - Utilities | Design | Quality | Plot Plan & Equipment Arrangement - Utilities | Orient plot plan / equipment arrangement to best utilize existing infrastructure and minimize cost of electrical and piping tie-ins. | Tom Bullington (KBR)
1541 | Plot Plan & Equipment Arrangement - Utilities | Other | Plot Plan & Equipment Arrangement - Utilities | Design | Quality | Plot Plan & Equipment Arrangement - Utilities | Consider underground utilities on above ground equipment location. Also consider impact on construction equipment. | Tom Bullington (KBR)
1542 | Procurement and Contracting - Contracts | Admin | Procurement and Contracting - Contracts | Project Management | Quality | Procurement and Contracting - Contracts | Ensure that an adequate number of competent field personnel have been selected to administer the fieldwork. Screen personnel to determine their expertise in contracting of work. | Tom Bullington (KBR)
1543 | Procurement and Contracting - Contracts | Admin | Procurement and Contracting - Contracts | Project Management | Quality | Procurement and Contracting - Contracts | Review the Project Procedures Manual for site specific requirements. Use BE&K Contract Management Manual. Incorporate Project Labor Agreement, if applicable. | Tom Bullington (KBR)
1544 | Procurement and Contracting - Contracts | Admin | Procurement and Contracting - Contracts | Project Management | Quality | Procurement and Contracting - Contracts | Establish a drawing distribution system to ensure that new or revised drawings are delivered to the contractors) in a timely manner without causing delays to the work. | Tom Bullington (KBR)
1545 | Procurement and Contracting - Contracts | Admin | Procurement and Contracting - Contracts | Project Management | Quality | Procurement and Contracting - Contracts | Ensure that a pre-bid / pre-award job walk and constructability meeting are required for the project. | Tom Bullington (KBR)
1546 | Procurement and Contracting - Contracts | Admin | Procurement and Contracting - Contracts | Project Management | Quality | Procurement and Contracting - Contracts | Develop a list of qualified contractors, for review with [Client], to bid each work package. | Tom Bullington (KBR)
1547 | Procurement and Contracting - Contracts | Admin | Procurement and Contracting - Contracts | Project Management | Quality | Procurement and Contracting - Contracts | Establish procedure, which allows for both lump sum and cost reimbursable strategy with applicable unit rates or time and materials in situations resulting in late material deliveries or scope changes. | Tom Bullington (KBR)
1548 | Procurement and Contracting - Contracts | Admin | Procurement and Contracting - Contracts | Project Management | Quality | Procurement and Contracting - Contracts | Include detailed schedule in the contract package with sufficient detail so that the contractor's price can include a commitment to schedule. | Tom Bullington (KBR)
1549 | Procurement and Contracting - Contracts | Admin | Procurement and Contracting - Contracts | Project Management | Quality | Procurement and Contracting - Contracts | Ensure that the project schedule is achievable and includes float for contingencies. | Tom Bullington (KBR)
1550 | Procurement and Contracting - Contracts | Admin | Procurement and Contracting - Contracts | Project Management | Quality | Procurement and Contracting - Contracts | Ensure that scheduling and progress reporting requirements imposed on contractors) are clearly defined and included in the Scope of Work. | Tom Bullington (KBR)
1551 | Procurement and Contracting - Contracts | Admin | Procurement and Contracting - Contracts | Project Management | Quality | Procurement and Contracting - Contracts | Ensure that suppliers are furnished a list of priorities for supply and delivery. | Tom Bullington (KBR)
1552 | Procurement and Contracting - Contracts | Admin | Procurement and Contracting - Contracts | Project Management | Quality | Procurement and Contracting - Contracts | Build time contingency between the supplier's forecast date and the contractor's commitment date to ensure adequate allowance for material and deliveries. | Tom Bullington (KBR)
1553 | Procurement and Contracting - Contracts | Admin | Procurement and Contracting - Contracts | Project Management | Quality | Procurement and Contracting - Contracts | Amend contracts in a timely and equitable manner to reflect authorized and approved changes. | Tom Bullington (KBR)
1554 | Procurement and Contracting - Contracts | Admin | Procurement and Contracting - Contracts | Project Management | Quality | Procurement and Contracting - Contracts | Finalize a list of all work that will be contracted. | Tom Bullington (KBR)
1555 | Procurement and Contracting - Contracts | Admin | Procurement and Contracting - Contracts | Project Management | Quality | Procurement and Contracting - Contracts | Man-load the schedule to obtain proper craft density and optimize productivity. | Tom Bullington (KBR)
1556 | Procurement and Contracting - Contracts | Admin | Procurement and Contracting - Contracts | Project Management | Quality | Procurement and Contracting - Contracts | Ensure the Scope of Work is well defined and the following requirements are included in the Contract plan: latest specifications, drawings and technical data - performanc requirements are clearly stated (i.e. hydro test, cleanup documentation and as build drawings. Additionally, the Code compliance rquirements are clearly stated, Interference responsibilities are deinfed, QA/QC reequiements care clearly defined, work areas / lay-down areas are clearly defined, the responsibility for supplying documentaion (.e. hydro test documentation, as-built drawings and safety record. | Tom Bullington (KBR)
1557 | Procurement and Contracting - Contracts | Admin | Procurement and Contracting - Contracts | Project Management | Quality | Procurement and Contracting - Contracts | Include a provision in the Contract for weekly contractor interface meetings to coordinate activities among various contractors and to discuss progress. | Tom Bullington (KBR)
1558 | Procurement and Contracting - Contracts | Admin | Procurement and Contracting - Contracts | Project Management | Quality | Procurement and Contracting - Contracts | Establish a procedure for tracking and documenting contractor performance. | Tom Bullington (KBR)
1559 | Procurement and Contracting - Contracts | Admin | Procurement and Contracting - Contracts | Project Management | Quality | Procurement and Contracting - Contracts | Develop a claims avoidance plan. | Tom Bullington (KBR)
1560 | Procurement and Contracting - Equipment | Admin | Procurement and Contracting - Equipment | Design | Quality | Procurement and Contracting - Equipment | Check equipment flange bolt holes for correct orientation/straddle of centerline at shop, especially on foreign made equipment. | Tom Bullington (KBR)
1561 | Procurement and Contracting - General | Admin | Procurement and Contracting - General | Design | Quality | Procurement and Contracting - General | Make project survey of suppliers and develop a list of suppliers with good track records. | Tom Bullington (KBR)
1562 | Procurement and Contracting - General | Admin | Procurement and Contracting - General | Design | Quality | Procurement and Contracting - General | Consider implementation of a supplier expediting program or procedure. | Tom Bullington (KBR)
1563 | Procurement and Contracting - General | Admin | Procurement and Contracting - General | Design | Quality | Procurement and Contracting - General | Establish shop inspection program. | Tom Bullington (KBR)
1564 | Procurement and Contracting - General | Admin | Procurement and Contracting - General | Design | Quality | Procurement and Contracting - General | Audit Project Engineering for completeness of drawings to ensure that suppliers are getting quality engineering drawings. | Tom Bullington (KBR)
1565 | Procurement and Contracting - General | Admin | Procurement and Contracting - General | Design | Quality | Procurement and Contracting - General | Prior to award, survey supplier's shop to ensure that: | Tom Bullington (KBR)
1566 | Procurement and Contracting - General | Admin | Procurement and Contracting - General | Design | Quality | Procurement and Contracting - General | · Facilities are adequate and large enough to handle the work. | Tom Bullington (KBR)
1567 | Procurement and Contracting - General | Admin | Procurement and Contracting - General | Design | Quality | Procurement and Contracting - General | · Supplier has enough qualified supervisors, engineers, craftsmen, welders, and draftsmen. | Tom Bullington (KBR)
1568 | Procurement and Contracting - Piping & Structural Steel | Admin | Procurement and Contracting - Piping & Structural Steel | Design | Quality | Procurement and Contracting - Piping & Structural Steel | Protection of piping gasket faces at site will avoid costly leaks during hydro test and start-up. | Tom Bullington (KBR)
1569 | Procurement and Contracting - Piping & Structural Steel | Admin | Procurement and Contracting - Piping & Structural Steel | Design | Quality | Procurement and Contracting - Piping & Structural Steel | Priorities for shop fabricated piping will be established by construction. | Tom Bullington (KBR)
1570 | Procurement and Contracting - Piping & Structural Steel | Admin | Procurement and Contracting - Piping & Structural Steel | Design | Quality | Procurement and Contracting - Piping & Structural Steel | Assure early orders for long lead items and those not available to ensure arrival to meet erection schedule (i.e. valves, strainers, traps and fittings, hose coupling, spring support). | Tom Bullington (KBR)
1571 | Procurement and Contracting - Piping & Structural Steel | Admin | Procurement and Contracting - Piping & Structural Steel | Design | Quality | Procurement and Contracting - Piping & Structural Steel | Order underground valves and hydrants early. Completion of U/G Construction priority. | Tom Bullington (KBR)
1572 | Procurement and Contracting - Piping & Structural Steel | Admin | Procurement and Contracting - Piping & Structural Steel | Design | Quality | Procurement and Contracting - Piping & Structural Steel | Order ample supply of spare parts for items such as valves, hydrants, etc. | Tom Bullington (KBR)
1573 | Procurement and Contracting - Piping & Structural Steel | Admin | Procurement and Contracting - Piping & Structural Steel | Design | Quality | Procurement and Contracting - Piping & Structural Steel | Determine if pipe spools should be fabricated on-site or off-site. | Tom Bullington (KBR)
1574 | Procurement and Contracting - Piping & Structural Steel | Admin | Procurement and Contracting - Piping & Structural Steel | Design | Quality | Procurement and Contracting - Piping & Structural Steel | Provide early issue of types of metals/alloys to be utilized. | Tom Bullington (KBR)
1575 | Procurement and Contracting - Piping & Structural Steel | Admin | Procurement and Contracting - Piping & Structural Steel | Design | Quality | Procurement and Contracting - Piping & Structural Steel | Vendors who supply valves and other components should be selected not only by price. Past performance evaluations should be made. | Tom Bullington (KBR)
1576 | Procurement and Contracting - Piping & Structural Steel | Admin | Procurement and Contracting - Piping & Structural Steel | Design | Quality | Procurement and Contracting - Piping & Structural Steel | Run cost analysis on using all stainless steel for lube-oil systems. Clearly define cleaning procedure. Avoid bottom connections. | Tom Bullington (KBR)
1577 | Procurement and Contracting - Piping & Structural Steel | Admin | Procurement and Contracting - Piping & Structural Steel | Design | Quality | Procurement and Contracting - Piping & Structural Steel | Area color-coding (circumferential striping) should be used for shop fabricated spools and should be shown on each isometric. | Tom Bullington (KBR)
1578 | Procurement and Contracting - Piping & Structural Steel | Admin | Procurement and Contracting - Piping & Structural Steel | Design | Quality | Procurement and Contracting - Piping & Structural Steel | Set up tracking system for spool piece pre-fab prior to release of first isometric. | Tom Bullington (KBR)
1579 | Procurement and Contracting - Piping & Structural Steel | Admin | Procurement and Contracting - Piping & Structural Steel | Design | Quality | Procurement and Contracting - Piping & Structural Steel | Establish back charge procedure and unit rates for repairing mis-fabricated pipe, and include these requirements in the shop fabricated pipe purchase order. | Tom Bullington (KBR)
1580 | Protective Coatings - Equipment Insulation | Mechanical | Protective Coatings - Equipment Insulation | Design | Quality | Protective Coatings - Equipment Insulation | When possible, use removable blanket type insulation on equipment needing access. | Tom Bullington (KBR)
1581 | Protective Coatings - Equipment Insulation | Mechanical | Protective Coatings - Equipment Insulation | Design | Quality | Protective Coatings - Equipment Insulation | Consider maximum shop fabrication of equipment insulation. | Tom Bullington (KBR)
1582 | Protective Coatings - General | Mechanical | Protective Coatings - General | Design | Quality | Protective Coatings - General | Minimize field storage of insulation by selecting vendor who will deliver insulation in work packages. | Tom Bullington (KBR)
1583 | Protective Coatings - General | Mechanical | Protective Coatings - General | Design | Quality | Protective Coatings - General | Monitor field and shop installation and provide technical expertise as required. | Tom Bullington (KBR)
1584 | Protective Coatings - General | Mechanical | Protective Coatings - General | Design | Quality | Protective Coatings - General | Develop systems completion plans so that hydro testing and insulation can start early, thereby spreading the insulation scope over a longer period of time and reducing the peak number of insulators. | Tom Bullington (KBR)
1585 | Protective Coatings - General | Mechanical | Protective Coatings - General | Design | Quality | Protective Coatings - General | Specify structural steel coating requirements as early as possible. Consider galvanizing or cor-ten steel instead of paint. | Tom Bullington (KBR)
1586 | Protective Coatings - Insulation Specification | Mechanical | Protective Coatings - Insulation Specification | Design | Quality | Protective Coatings - Insulation Specification | Perform engineering cost / life study to determine most effective thickness of insulation for project. | Tom Bullington (KBR)
1587 | Protective Coatings - Insulation Specification | Mechanical | Protective Coatings - Insulation Specification | Design | Quality | Protective Coatings - Insulation Specification | Minimizes double layers of insulation, where possible. Use 4-inch layer instead of 2 layers of 2-inch. | Tom Bullington (KBR)
1588 | Protective Coatings - Insulation Specification | Mechanical | Protective Coatings - Insulation Specification | Design | Quality | Protective Coatings - Insulation Specification | Verify and detail with sketches the required "cutback" at flanges for bolt removal. Also, identify flanges that are required by specification to be insulated. | Tom Bullington (KBR)
1589 | Protective Coatings - Insulation Specification | Mechanical | Protective Coatings - Insulation Specification | Design | Quality | Protective Coatings - Insulation Specification | Review and verify supplier insulation requirements and specifications for compliance with project specifications and at interface points. | Tom Bullington (KBR)
1590 | Protective Coatings - Paint Application | Mechanical | Protective Coatings - Paint Application | Design | Quality | Protective Coatings - Paint Application | Develop a plan for painting tops of beams and outside of purlins and girts prior to installation of items such as floor plates, grating, siding, and roof decks. | Tom Bullington (KBR)
1591 | Protective Coatings - Paint Application | Mechanical | Protective Coatings - Paint Application | Design | Quality | Protective Coatings - Paint Application | Require by pipe or equipment support details and painting specifications that all Teflon surfaces be protected during construction and painting operations. | Tom Bullington (KBR)
1592 | Protective Coatings - Paint Application | Mechanical | Protective Coatings - Paint Application | Design | Quality | Protective Coatings - Paint Application | If inorganic zinc primer is specified, inspect and verify the application of this material. Suppliers and other applicators, require specific advice/instructions on using this material. | Tom Bullington (KBR)
1593 | Protective Coatings - Paint Application | Mechanical | Protective Coatings - Paint Application | Design | Quality | Protective Coatings - Paint Application | Specify and monitor all sandblasting materials and their application. | Tom Bullington (KBR)
1594 | Protective Coatings - Paint Application | Mechanical | Protective Coatings - Paint Application | Design | Quality | Protective Coatings - Paint Application | Specify, monitor, and inspect all pipe wrap and internal coatings applications. | Tom Bullington (KBR)
1595 | Protective Coatings - Paint Application | Mechanical | Protective Coatings - Paint Application | Design | Quality | Protective Coatings - Paint Application | Develop a program for shop painting of structural members, pipe spools, and equipment. | Tom Bullington (KBR)
1596 | Protective Coatings - Paint Specifications | Mechanical | Protective Coatings - Paint Specifications | Design | Quality | Protective Coatings - Paint Specifications | Develop paint specifications, including the required color schemes, early in the project so that steel, pipe, and equipment can be painted in supplier shops (standardize colors). | Tom Bullington (KBR)
1597 | Protective Coatings - Paint Specifications | Mechanical | Protective Coatings - Paint Specifications | Design | Quality | Protective Coatings - Paint Specifications | Require supplier painting and inspection methods for surface preparation to be compatible with the [Client]'s specifications. Use manufacturer's standard finish, if specifications allow. | Tom Bullington (KBR)
1598 | Protective Coatings - Paint Specifications | Mechanical | Protective Coatings - Paint Specifications | Design | Quality | Protective Coatings - Paint Specifications | Consider ambient temperature and relative humidity conditions that will be encountered during construction, as well as during plant life, when specifying paint for field application. | Tom Bullington (KBR)
1599 | Protective Coatings - Paint Specifications | Mechanical | Protective Coatings - Paint Specifications | Design | Quality | Protective Coatings - Paint Specifications | Consider compatibility and maximum time allowed between application of shop and field applied systems when specifying paint for shop primers and field-finish coats. | Tom Bullington (KBR)
1600 | Protective Coatings - Paint Specifications | Mechanical | Protective Coatings - Paint Specifications | Design | Quality | Protective Coatings - Paint Specifications | Consider maximum operating or upset temperatures and steam-out requirements when specifying paints. | Tom Bullington (KBR)
1601 | Protective Coatings - Paint Specifications | Mechanical | Protective Coatings - Paint Specifications | Design | Quality | Protective Coatings - Paint Specifications | Standardize primer and finish coat paint types to the greatest extent practical. | Tom Bullington (KBR)
1602 | Protective Coatings - Pipe Insulation | Mechanical | Protective Coatings - Pipe Insulation | Design | Quality | Protective Coatings - Pipe Insulation | Standardize, where cost allows, the different thickness if insulation (i.e., need 10,000 LF of 2 inch thick mineral wool for 6 inch pipe and 100 LF of 1 1/2 inch thick mineral wool for 6 inch pipe - specify all 6 inch pipe mineral wool 2 inches thick). | Tom Bullington (KBR)
1603 | Protective Coatings - Pipe Insulation | Mechanical | Protective Coatings - Pipe Insulation | Design | Quality | Protective Coatings - Pipe Insulation | Use in specification mineral wool versus calcium silica where possible | Tom Bullington (KBR)
1604 | Protective Coatings - Pipe Insulation | Mechanical | Protective Coatings - Pipe Insulation | Design | Quality | Protective Coatings - Pipe Insulation | Piping system on vessels and heaters, plan insulation with piping and mechanical to eliminate interference and prevent inaccessible process controls. | Tom Bullington (KBR)
1605 | Protective Coatings - Special Insulation Applications | Mechanical | Protective Coatings - Special Insulation Applications | Design | Quality | Protective Coatings - Special Insulation Applications | If applicable, review and approve all special insulation applications, such as ducts, packaged units and insulation used as fireproofing. | Tom Bullington (KBR)
1606 | Protective Coatings - Special Insulation Applications | Mechanical | Protective Coatings - Special Insulation Applications | Design | Quality | Protective Coatings - Special Insulation Applications | Verify and include specified insulation requirements for electrical and control cable systems and special valves. | Tom Bullington (KBR)
1607 | Protective Coatings - Special Insulation Applications | Mechanical | Protective Coatings - Special Insulation Applications | Design | Quality | Protective Coatings - Special Insulation Applications | Be sure all steam and electric cable tracing requirements are considered when making material takeoffs. | Tom Bullington (KBR)
1608 | Steel - Fabrication | Civil | Steel - Fabrication | Design | Quality | Steel - Fabrication | Obtain construction input for establishing delivery sequence. | Tom Bullington (KBR)
1609 | Steel - Fabrication | Civil | Steel - Fabrication | Design | Quality | Steel - Fabrication | Review delivery sequence. Concentrate efforts toward and release of drawings in accordance with Construction agreed priorities. Detail erectable steel. | Tom Bullington (KBR)
1610 | Steel - Fabrication | Civil | Steel - Fabrication | Design | Quality | Steel - Fabrication | Apply fireproofing in the fabrication shop where practical. | Tom Bullington (KBR)
1611 | Steel - Fabrication | Civil | Steel - Fabrication | Design | Quality | Steel - Fabrication | Check miscellaneous steelwork items such as equipment frames, architectural items, grounding clips, etc., that don't appear on Structural drawings. Ensure these items are included in scope of supplier, contract packages or POs. | Tom Bullington (KBR)
1612 | Steel - Fireproofing & Coating | Civil | Steel - Fireproofing & Coating | Design | Quality | Steel - Fireproofing & Coating | Consider utilizing galvanized structural and miscellaneous steel. | Tom Bullington (KBR)
1613 | Steel - Fireproofing & Coating | Civil | Steel - Fireproofing & Coating | Design | Quality | Steel - Fireproofing & Coating | Ensure that responsibility for galvanizing structural and miscellaneous steel is specified in design and Contract documents. | Tom Bullington (KBR)
1614 | Steel - Fireproofing & Coating | Civil | Steel - Fireproofing & Coating | Design | Quality | Steel - Fireproofing & Coating | Finish-coat all non-galvanized/fireproofed steel. As a minimum primer and first intermediate coat. | Tom Bullington (KBR)
1615 | Steel - Fireproofing & Coating | Civil | Steel - Fireproofing & Coating | Design | Quality | Steel - Fireproofing & Coating | Review dimensions of fireproofing with fabricator and standardize dimensions. | Tom Bullington (KBR)
1616 | Steel - Fireproofing & Coating | Civil | Steel - Fireproofing & Coating | Design | Quality | Steel - Fireproofing & Coating | Ensure that field connections can be made outside of fireproofing. | Tom Bullington (KBR)
1617 | Steel - Fireproofing & Coating | Civil | Steel - Fireproofing & Coating | Design | Quality | Steel - Fireproofing & Coating | Standardize fireproofing types and details. | Tom Bullington (KBR)
1618 | Steel - Fireproofing & Coating | Civil | Steel - Fireproofing & Coating | Design | Quality | Steel - Fireproofing & Coating | Use lightweight Cementitious or pryrocrete materials for fireproofing of structural steel. | Tom Bullington (KBR)
1619 | Steel - Fireproofing & Coating | Civil | Steel - Fireproofing & Coating | Design | Quality | Steel - Fireproofing & Coating | Define fireproofing requirements early on and make sure contractor understands scope. | Tom Bullington (KBR)
1620 | Steel - General | Civil | Steel - General | Design | Quality | Steel - General | Minimize or eliminate the use of through-web beam connection. If this type connection is required, place seat angles on columns. | Tom Bullington (KBR)
1621 | Steel - General | Civil | Steel - General | Design | Quality | Steel - General | Eliminate use of boxed-in connections. | Tom Bullington (KBR)
1622 | Steel - Pre-Assembly | Civil | Steel - Pre-Assembly | Design | Quality | Steel - Pre-Assembly | Modularization of pipe racks requires review of practicality of fabrication of lengths up to 30 meters and install with the pipe rack steel, as the tiers of the rack are installed (Include stream tracing). | Tom Bullington (KBR)
1623 | Steel - Pre-Assembly | Civil | Steel - Pre-Assembly | Design | Quality | Steel - Pre-Assembly | Detail High Bay Steel in a manner that will allow fabrication of roof system at grounded level. | Tom Bullington (KBR)
1624 | Steel - Pre-Assembly | Civil | Steel - Pre-Assembly | Design | Quality | Steel - Pre-Assembly | Engineer should provide Rack Stuffing Drawings for pipe rack erection and modularization planning. | Tom Bullington (KBR)
1625 | Steel - Stairs, Ladders & Platforms | Civil | Steel - Stairs, Ladders & Platforms | Design | Quality | Steel - Stairs, Ladders & Platforms | Design and erect permanent stairways, platforms, and ladders as soon as practical. | Tom Bullington (KBR)
1626 | Steel - Stairs, Ladders & Platforms | Civil | Steel - Stairs, Ladders & Platforms | Design | Quality | Steel - Stairs, Ladders & Platforms | Provide adequate ladders, stairways and platforms for operators and maintenance personnel to access and perform required work on production equipment. Design should include consideration for tools, material, spare parts and repair equipment requirements. | Tom Bullington (KBR)
1627 | Steel - Stairs, Ladders & Platforms | Civil | Steel - Stairs, Ladders & Platforms | Design | Quality | Steel - Stairs, Ladders & Platforms | Pre-assemble in shop, to the largest extent possible, ladders, stairways, catwalks and miscellaneous platforms. | Tom Bullington (KBR)
1628 | Steel - Stairs, Ladders & Platforms | Civil | Steel - Stairs, Ladders & Platforms | Design | Quality | Steel - Stairs, Ladders & Platforms | Investigate the use of various manufactured systems for handrails and free standing, pre-engineered stair towers. | Tom Bullington (KBR)
1629 | Steel - Stairs, Ladders & Platforms | Civil | Steel - Stairs, Ladders & Platforms | Design | Quality | Steel - Stairs, Ladders & Platforms | Cut and band in the shop holes required in grating for pipe penetrations. | Tom Bullington (KBR)
1630 | Steel - Stairs, Ladders & Platforms | Civil | Steel - Stairs, Ladders & Platforms | Design | Quality | Steel - Stairs, Ladders & Platforms | Maximize the use of grating floor systems in lieu of floor plate, whenever possible. | Tom Bullington (KBR)
1631 | Steel - Stairs, Ladders & Platforms | Civil | Steel - Stairs, Ladders & Platforms | Design | Quality | Steel - Stairs, Ladders & Platforms | Standardize hole sizes in grating for pipe penetrations. | Tom Bullington (KBR)
1632 | Roof edges (construction, maintenance) | Architectural | Building exterior | Design | Safety | Falling | Preferably design minimum 3' 6" height parapets or railings at all roof edges. Alternatively, provide safety line tie-off points along all roof edges. | Washington Group (Rick Callor) Haskell (David Engdahl)
1633 | Pre-engineered metal building roofs | Architectural | Building exterior | Design | Safety | Falling. | Provide tie off loops as part of building package. | Washington Group (Rick Callor) Haskell (David Engdahl)
1634 | Roof openings (hatches, skylights, shafts, equipment openings) | Architectural | Building exterior | Design | Safety | Falling | Design permanent grating in opening, to be installed when opening is created during construction. | Washington Group (Rick Callor) Haskell (David Engdahl)
1635 | Roof access | Architectural | Building exterior | Design | Safety | Falling | Provide safe permanent access to roofs, in order of preference: Stair. Ships ladder. OSHA ladder. | Washington Group (Rick Callor) Haskell (David Engdahl)
1636 | Blind exit passageways, vehicular exit ways | Architectural | Building exterior | Design | Safety | Struck by | Avoid if possible. Provide mirrors, warning bells or other warning devices. | Washington Group (Rick Callor) Haskell (David Engdahl)
1637 | Loose materials and equipment | Architectural | Building exterior | Design | Safety | Struck by | Avoid loose or unanchored materials or equipment, especially in high wind areas. | Washington Group (Rick Callor) Haskell (David Engdahl)
1638 | Changes in roof elevations | Architectural | Building exterior | Design | Safety | Falling | Provide safe access directly to all roof levels or from level to level (protected ladder, ships ladder, stairs). | Washington Group (Rick Callor) Haskell (David Engdahl)
1639 | Vehicular deck load limits | Architectural | Building exterior | Design | Safety | Structural failure | Load limit signage. Provide physical height limit barrier as fail-safe prevention of vehicular overloading. Card or code access system. Car count system. | Washington Group (Rick Callor) Haskell (David Engdahl)
1640 | Exterior stairs, ramps, pedestrian walks | Architectural | Building exterior | Design | Safety | Slipping, falling | Provide slip resistant floor materials. Provide guardrails. In cold climates, consider ice melting cabling. | Washington Group (Rick Callor) Haskell (David Engdahl)
1641 | Snow, ice accumulation | Architectural | Building exterior | Design | Safety | Slipping, falling | Use slip resistant materials. Use snow melting cables. Minimize slopes. | Washington Group (Rick Callor) Haskell (David Engdahl)
1642 | Dock door edge protection | Architectural | Building exterior | Design | Safety | Falling | Safety striping. Provide forklift protective edge. Consider trailer restraints. Signage. | Washington Group (Rick Callor) Haskell (David Engdahl)
1643 | Impact resistance at openings | Architectural | Building exterior | Design | Safety | Struck by | In high wind areas, provide impact resistant windows, doors and at other openings at occupied spaces. | Washington Group (Rick Callor) Haskell (David Engdahl)
1644 | Window washing | Architectural | Building exterior | Design | Safety | Falling | Make provisions for scaffolding or tie-offs. | Washington Group (Rick Callor) Haskell (David Engdahl)
1645 | Emergency building evacuation | Architectural | Building exterior | Design | Safety | Lack of safe havens | Identify evacuation assembly/communication points on site. | Washington Group (Rick Callor) Haskell (David Engdahl)
1646 | Furnishings general | Architectural | Furninshings and Equipment | Design | Safety | Overturning, falling, cuts | Provide furnishings which are balanced and not subject to overturning. Check furnishings prior to installation for sharp edges and for areas which may catch clothing or pinch fingers. | Washington Group (Rick Callor) Haskell (David Engdahl)
1647 | Cabinet/locker door handles | Architectural | Furninshings and Equipment | Design | Safety | Struck by | Provide recessed handles. | Washington Group (Rick Callor) Haskell (David Engdahl)
1648 | Hoists and cranes | Architectural | Furninshings and Equipment | Design | Safety | Struck by | Provide safety operation instructions and warning signs. | Washington Group (Rick Callor) Haskell (David Engdahl)
1649 | Playground equipment | Architectural | Furninshings and Equipment | Design | Safety | Falling, caught between | Provide adequate safety standards for specified equipment. | Washington Group (Rick Callor) Haskell (David Engdahl)
1650 | Furnishings/equipment in seismic areas | Architectural | Furninshings and Equipment | Design | Safety | Struck by | Properly anchor furnishings and equipment. | Washington Group (Rick Callor) Haskell (David Engdahl)
1651 | Mezzanine deck load limits | Architectural | Building interior | Design | Safety | Structural failure | Provide maximum floor load capacity warning signs. | Washington Group (Rick Callor) Haskell (David Engdahl)
1652 | Forklift circulation | Architectural | Building interior | Design | Safety | Struck by | Provide pedestrian circulation safety markings. Provide bollards/guardrails at potential pedestrian/ forklift conflict areas. Provide separate pedestrian circulation doors. | Washington Group (Rick Callor) Haskell (David Engdahl)
1653 | Floor level changes | Architectural | Building interior | Design | Safety | Tripping, falling | Provide warning markings and/or color change. | Washington Group (Rick Callor) Haskell (David Engdahl)
1654 | Floor expansion joints | Architectural | Building interior | Design | Safety | Tripping, falling | Provide safe walking surface joint covers. | Washington Group (Rick Callor) Haskell (David Engdahl)
1655 | Finish material change. | Architectural | Building interior | Design | Safety | Tripping. | Provide transition strips. | Washington Group (Rick Callor) Haskell (David Engdahl)
1656 | Stair tread and landing nosings | Architectural | Building interior | Design | Safety | Tripping, falling | Provide slip resistant nosings. | Washington Group (Rick Callor) Haskell (David Engdahl)
1657 | Low headroom protrusions | Architectural | Building interior | Design | Safety | Struck by | Provide warning sign, soft protective material. | Washington Group (Rick Callor) Haskell (David Engdahl)
1658 | Confined spaces | Architectural | Building interior | Design | Safety | Caught against | Provide warning signs. Provide emergency call devices. | Washington Group (Rick Callor) Haskell (David Engdahl)
1659 | Welding areas, arc flash | Architectural | Building interior | Design | Safety | Burns, asphyxiation, eye damage | Provide flame protection, eye protection devices and proper exhaust system. | Washington Group (Rick Callor) Haskell (David Engdahl)
1660 | Dust generating environments | Architectural | Building interior | Design | Safety | Explosion | Provide dust removal system. Provide warning signs. | Washington Group (Rick Callor) Haskell (David Engdahl)
1661 | Smoke generating materials | Architectural | Building interior | Design | Safety | Asphyxiation | Avoid smoke generating materials. | Washington Group (Rick Callor) Haskell (David Engdahl)
1662 | Harmful emissions from finishes (paint voc's, carpet, etc.) | Architectural | Building interior | Design | Safety | Respiratory illness | Specify low emission products. | Washington Group (Rick Callor) Haskell (David Engdahl)
1663 | Floor opening | Architectural | Building interior | Design | Safety | Fall from elevation | Group small floor openings together to create one large opening. Provide permanent guardrails. | Washington Group (Rick Callor) Haskell (David Engdahl)
1664 | Flooring in wet areas (exterior tile, wash down areas, kitchens, etc.) | Architectural | General | Design | Safety | Slipping | Provide slip resistant floor materials. | Washington Group (Rick Callor) Haskell (David Engdahl)
1665 | Blind door swings | Architectural | General | Design | Safety | Struck by, caught against | Avoid if possible. Provide mirrors, warning bells or other warning devices. | Washington Group (Rick Callor) Haskell (David Engdahl)
1666 | Presence of dangerous materials (acid waste, asbestos, bio-hazard, poisons, lab waste) | Architectural | General | Design | Safety | Burns, contamination, asphyxiation, poisoning | Provide warning signs. Provide adequate fume ventilation. Engage specialists to handle dangerous materials. | Washington Group (Rick Callor) Haskell (David Engdahl)
1667 | Fixed ladders | Architectural | General | Design | Safety | Falling | Provide other means (ships ladder, stairs) if possible. Follow OSHA Safety Standards (cage, rest landings, extended handrails). | Washington Group (Rick Callor) Haskell (David Engdahl)
1668 | Low planter walls in pedestrian areas | Architectural | General | Design | Safety | Tripping, falling | Avoid low walls in circulation areas. Use furniture barrier. Avoid hidden alcoves and offsets. | Washington Group (Rick Callor) Haskell (David Engdahl)
1669 | Parking garage personal safety | Architectural | General | Design | Safety | Personal attack | Provide view windows in doors. Provide emergency call devices. Enhance lighting. Maximize view from street. | Washington Group (Rick Callor) Haskell (David Engdahl)
1670 | Lock-in, lock-out | Architectural | General | Design | Safety | Trapped for extended periods | Check hardware for safe egress operation. Provide emergency call devices. | Washington Group (Rick Callor) Haskell (David Engdahl)
1671 | Handrail design | Architectural | General | Design | Safety | Caught, cut | Check handrails design and detailing for avoidance of potential finger and hand injuries. | Washington Group (Rick Callor) Haskell (David Engdahl)
1672 | Door sidelights | Architectural | General | Design | Safety | Run into | Provide horizontal muntin bars, base or markings to deter people from walking into glass sidelights, even if tempered. | Washington Group (Rick Callor) Haskell (David Engdahl)
1673 | Balcony railings, open stairs | Architectural | General | Design | Safety | Falling | Provide guardrail height railings. | Washington Group (Rick Callor) Haskell (David Engdahl)
1674 | Overhead construction | Architectural | General | Design | Safety | Falling, struck by | Design components to facilitate prefabrication at grade and erection as complete assemblies. | Washington Group (Rick Callor) Haskell (David Engdahl)
1675 | Floor plan layout | Architectural | General | Design | Safety | Falling | Minimize number of offsets in building plan and make offsets a consistent size and as large as possible to simplify work area for construction workers. | Washington Group (Rick Callor) Haskell (David Engdahl)
1676 | Tornado protection | Architectural | General | Design | Safety | Wind blown debris | Provide secure tornado shelter of 5 s.f./person in tornado prone areas. | Washington Group (Rick Callor) Haskell (David Engdahl)
1677 | Isolated structures | Architectural | General | Design | Safety | Personal safety in emergencies | Provide emergency call system where persons work alone. | Washington Group (Rick Callor) Haskell (David Engdahl)
1678 | Demolition | Architectural | General | Design | Safety | Collapse | Note bearing walls on drawings. | Washington Group (Rick Callor) Haskell (David Engdahl)
1679 | Clearances | Electrical | Lighting | Design | Safety | Trapped by electrical fire | Provide code clearances, escape path(s). Consider increases to code clearances. | Washington Group (Rick Callor) Haskell (David Engdahl)
1680 | Parking structures | Electrical | Lighting | Design | Safety | Personal safety | Provide safe lighting levels, including access. Consider exceeding IES recommendations. Consider emergency warning call system. Consider security systems. | Washington Group (Rick Callor) Haskell (David Engdahl)
1681 | Attics, crawl spaces, catwalks, mezzanines | Electrical | Lighting | Design | Safety | Fall | Provide safe lighting levels, including access. Consider indicating pathways and adding tie-offs. | Washington Group (Rick Callor) Haskell (David Engdahl)
1682 | Roof with equipment | Electrical | Lighting | Design | Safety | Fall | Provide safe lighting levels, including access. | Washington Group (Rick Callor) Haskell (David Engdahl)
1683 | Floor level changes in elevation | Electrical | Lighting | Design | Safety | Tripping, falls | Provide safe lighting levels. Consider exceeding IES recommendations. Consider warning light(s). | Washington Group (Rick Callor) Haskell (David Engdahl)
1684 | Electrical luminaires in seismic areas | Electrical | Lighting | Design | Safety | Struck by | Properly anchor and/or support electrical equipment. | Washington Group (Rick Callor) Haskell (David Engdahl)
1685 | All lighting in stairwells | Electrical | Lighting | Design | Safety | Fall | Mount emergency lighting in stairwells to be easily accessible, and avoid locations over treads. | Washington Group (Rick Callor) Haskell (David Engdahl)
1686 | High location luminaires | Electrical | Lighting | Design | Safety | Fall | Locate to be easily accessible by maintenance staff. | Washington Group (Rick Callor) Haskell (David Engdahl)
1687 | Temporary lighting | Electrical | Lighting | Design | Safety | Fall | Specify to be maintained at all times with bulb guards, unbroken lamps, safe wiring, and grounding. | Washington Group (Rick Callor) Haskell (David Engdahl)
1688 | Site/ground mounted lighting | Electrical | Lighting | Design | Safety | Burn | Locate out of personnel area. Consider specifying better guard. | Washington Group (Rick Callor) Haskell (David Engdahl)
1689 | Lighting control points for first employee or power outage | Electrical | Lighting | Design | Safety | Fall | Place light switches in best location based on circulation pattern and best viewpoint. | Washington Group (Rick Callor) Haskell (David Engdahl)
1690 | Clearances | Electrical | Power | Design | Safety | Trapped by electrical fire | Provide code clearances, escape path(s). Consider increases to code clearances. | Washington Group (Rick Callor) Haskell (David Engdahl)
1691 | Isolated structures | Electrical | Power | Design | Safety | Personal safety in emergency | Provide emergency call system where personnel work alone. Consider additional signage, security monitoring, or buddy system regulations. | Washington Group (Rick Callor) Haskell (David Engdahl)
1692 | Window washing | Electrical | Power | Design | Safety | Electrocution | Provide adequate and easily accessible power for window washing system. | Washington Group (Rick Callor) Haskell (David Engdahl)
1693 | Pedestal type floor mounted electrical devices | Electrical | Power | Design | Safety | Trip | Locate out of traffic areas or use flush electrical boxes. | Washington Group (Rick Callor) Haskell (David Engdahl)
1694 | Wet areas electrical devices | Electrical | Power | Design | Safety | Electrocution | Use GFI and/or locate in dry areas, per code or exceed code. | Washington Group (Rick Callor) Haskell (David Engdahl)
1695 | Explosion hazard electrical devices | Electrical | Power | Design | Safety | Explosion | Use code mandated, UL approved electrical equipment and design per codes. | Washington Group (Rick Callor) Haskell (David Engdahl)
1696 | Snow melting of handicap pathways | Electrical | Power | Design | Safety | Fall | Include snow melting system for handicap ramps and open stoops. | Washington Group (Rick Callor) Haskell (David Engdahl)
1697 | Lockout provisions | Electrical | Power | Design | Safety | Electrocution | Design electrical systems components with lockout capability and readily accessible. | Washington Group (Rick Callor) Haskell (David Engdahl)
1698 | Disconnects and controls identification | Electrical | Power | Design | Safety | Electrocution | Design and install signage readable from 4 feet. | Washington Group (Rick Callor) Haskell (David Engdahl)
1699 | Electrical equipment in shops, process, refrigeration rooms | Electrical | Power | Design | Safety | Electrocution, fire | Provide emergency shutoff system/button. | Washington Group (Rick Callor) Haskell (David Engdahl)
1700 | Electrical equipment in seismic areas | Electrical | Power | Design | Safety | Struck by | Properly anchor and/or support electrical equipment. | Washington Group (Rick Callor) Haskell (David Engdahl)
1701 | Temporary power, portable welders, generator receptacles | Electrical | Power | Design | Safety | Electrocution | Specify GFI required on all 120V receptacles. | Washington Group (Rick Callor) Haskell (David Engdahl)
1702 | Energized electrical equipment (including data/signal systems over 50V) | Electrical | Power | Design | Safety | Electrocution | Specify all energized electrical equipment rooms shall have signage (for example "Danger - Authorized Personnel Only - High Voltage") and all energized electrical panels to be maintained with dead front covers in place. | Washington Group (Rick Callor) Haskell (David Engdahl)
1703 | Energized electrical equipment | Electrical | Power | Design | Safety | Electrocution | Only qualified/authorized electricians will be permitted to work on energized electrical equipment. | Washington Group (Rick Callor) Haskell (David Engdahl)
1704 | Grounding | Electrical | Power | Design | Safety | Electrocution | Verify grounding system design is clearly delineated. | Washington Group (Rick Callor) Haskell (David Engdahl)
1705 | High mounted electrical equipment/ systems | Electrical | Power | Design | Safety | Fall | Design to allow ease of pre-fabricated assemblies (assemble at floor level, raise to high mounting heights) Consider wall mounted equipment or access platform. | Washington Group (Rick Callor) Haskell (David Engdahl)
1706 | Large equipment delivery | Electrical | Power | Design | Safety | Caught by | Verify pathway is clear and adequate to allow major equipment to be delivered and placed into proper location. Consider larger doors/corridors, and/or specifying equipment shipping breaks. | Washington Group (Rick Callor) Haskell (David Engdahl)
1707 | Start-up | Electrical | Power | Design | Safety | Electrocution | Require procedures/checklists for systematically starting and energizing items | Washington Group (Rick Callor) Haskell (David Engdahl)
1708 | Clearances | Electrical | Site | Design | Safety | Trapped by electrical fire | Provide code clearances, escape path(s). Consider increases to code clearances. | Washington Group (Rick Callor) Haskell (David Engdahl)
1709 | Steep slopes and embankments | Electrical | Site | Design | Safety | Service vehicle and pedestrian falls | Avoid steep slopes. If unavoidable, provide protective rails and barriers. | Washington Group (Rick Callor) Haskell (David Engdahl)
1710 | Outdoor transformers, switchboards, and generators | Electrical | Site | Design | Safety | Terrorist attacks | For public or other buildings particularly vulnerable to terrorist attack, provide substantial vehicle limiting barriers (walls/bollards) at building. Consider placing indoors or UG. Consider 24 hour surveillance. | Washington Group (Rick Callor) Haskell (David Engdahl)
1711 | Outdoor transformers, switchboards, and generators | Electrical | Site | Design | Safety | Electrocution | Provide warning signs. Consider fencing or other methods to restrict access. Verify locks on enclosures. | Washington Group (Rick Callor) Haskell (David Engdahl)
1712 | Manholes - potential fume build-up | Electrical | Site | Design | Safety | Asphyxiation | Provide safety warning signs at manhole. | Washington Group (Rick Callor) Haskell (David Engdahl)
1713 | Overhead power line conflicts | Electrical | Site | Design | Safety | Electrocution | Avoid locating overhead power lines near construction areas with cranes. Avoid potentially tall landscape materials near overhead power lines. | Washington Group (Rick Callor) Haskell (David Engdahl)
1714 | UG utility lines | Electrical | Site | Design | Safety | Cave-ins | Consider design of underground utilities to be placed using trenchless technologies. | Washington Group (Rick Callor) Haskell (David Engdahl)
1715 | UG utility lines | Electrical | Site | Design | Safety | Electrocution | Provide warning tape above cables/duct bank. Call for lock out/tag out of UG circuits. Call for record drawings to be correct and available. | Washington Group (Rick Callor) Haskell (David Engdahl)
1716 | Site parking lot | Electrical | Site | Design | Safety | Personal safety | Provide safe lighting levels. Consider exceeding IES recommendations. Consider emergency warning call system. | Washington Group (Rick Callor) Haskell (David Engdahl)
1717 | Site parking lot at changes in elevation | Electrical | Site | Design | Safety | Falls | Provide safe lighting levels. Consider exceeding IES recommendations. | Washington Group (Rick Callor) Haskell (David Engdahl)
1718 | Clearances | Electrical | Systems | Design | Safety | Trapped by electrical fire | Provide clearances/escape path(s). | Washington Group (Rick Callor) Haskell (David Engdahl)
1719 | Isolated structures | Electrical | Systems | Design | Safety | Personal safety in emergency | Provide emergency call system where personnel work alone. | Washington Group (Rick Callor) Haskell (David Engdahl)
1720 | Pedestal type floor mounted data/voice devices | Electrical | Systems | Design | Safety | Trip | Locate out of traffic areas or use flush boxes. | Washington Group (Rick Callor) Haskell (David Engdahl)
1721 | Electrical system equipment in seismic areas | Electrical | Systems | Design | Safety | Struck by | Properly anchor and/or support electrical system equipment. | Washington Group (Rick Callor) Haskell (David Engdahl)
1722 | Card readers/key pads | Electrical | Systems | Design | Safety | Personal safety | Locate to be in safe location and unreadable by criminals. | Washington Group (Rick Callor) Haskell (David Engdahl)
1723 | Fire alarm, security systems, CCTV systems | Electrical | Systems | Design | Safety | Personal safety | Provide training to building owner staff. | Washington Group (Rick Callor) Haskell (David Engdahl)
1724 | Exterior alarms | Electrical | Systems | Design | Safety | Personal safety | Consider providing exterior fire alarm horns, strobes, intrusion alarms. | Washington Group (Rick Callor) Haskell (David Engdahl)
1725 | High mounted electrical equipment/ systems | Electrical | Systems | Design | Safety | Fall | Design to allow ease of pre-fabricated assemblies (assemble at floor level, raise to high mounting heights). | Washington Group (Rick Callor) Haskell (David Engdahl)
1726 | Large equipment delivery | Electrical | Systems | Design | Safety | Caught by | Verify pathway is clear and adequate to allow major equipment to be delivered and placed into proper location. Consider larger doors/corridors, and/or specifying equipment shipping breaks. | Washington Group (Rick Callor) Haskell (David Engdahl)
1727 | Moving equipment that can cause crushing injuries such as fans and pumps. | Mechanical | Mechanical | Design | Safety | Caught in/between [Struck by /Against/Caught] | • Specify guards that protect from interference with moving parts on all equipment. • In high traffic or high risk areas, specify "yellow OSHA" guards. | Washington Group (Rick Callor) Haskell (David Engdahl)
1728 | Buried in trench while installing underground utilities. | Mechanical | Mechanical | Design | Safety | Cave-in [Cave-Ins] | • Where appropriate specify, pre-manufactured, systems that limit time in trench. • Where appropriate, avoid deep trenching. For example, review proposed invert locations and look for ways to minimize depth of utilities. | Washington Group (Rick Callor) Haskell (David Engdahl)
1729 | Trapped in a large vessel such as storage tank or manhole. | Mechanical | Mechanical | Design | Safety | Confined space [Asphyxiation - Confined Space] | • Specify that O&M manuals include protocol for entry into all confined spaces. • Where appropriate, provide signage for egress of confined spaces. • Where appropriate, provide ladders for more rapid egress. • Where appropriate, build in emergency/safety equipment. | Washington Group (Rick Callor) Haskell (David Engdahl)
1730 | Mechanical equipment sparking or electrical components arcing in explosive environments. | Mechanical | Mechanical | Design | Safety | Explosion | • Avoid locating mechanical equipment in explosive environments. • Specify explosion proof fans (e.g., aluminum in lieu of steel) and explosion-proof electrical components. | Washington Group (Rick Callor) Haskell (David Engdahl)
1731 | Shocked while maintaining electrical components of mechanical equipment such as duct heaters and exhaust fans. | Mechanical | Mechanical | Design | Safety | Electrical shock [Electrocution] | • Show equipment clearances required for working on electrical components. Take particular note of spaces anticipated to be tight for space such as components installed above ceilings or in chases. • Specify all equipment to be provided with minimum clearances required by code and in accordance with the manufacturer's requirements and recommendations. | Washington Group (Rick Callor) Haskell (David Engdahl)
1732 | Infection caused by legionella in domestic hot water system. | Mechanical | Mechanical | Design | Safety | Environmental climate (infection) | Store domestic hot water above 140 degrees F and mix to appropriate temperature, especially where hot water is used by immune sensitive individuals such as children or the infirm. | Washington Group (Rick Callor) Haskell (David Engdahl)
1733 | Hearing loss due to excessively noisy equipment | Mechanical | Mechanical | Design | Safety | Environmental climate (noise) | • Check sound levels of potentially noisy equipment (chillers, fans, etc.) • Avoid excessively noisy equipment (e.g., above 85 dba) that may require the use of hearing protection. | Washington Group (Rick Callor) Haskell (David Engdahl)
1734 | Falling off of roof while repairing or maintaining mechanical equipment. | Mechanical | Mechanical | Design | Safety | Falls [Slips/Falls] | • Avoid locating equipment less than 10' 0" from roof edge. • Where necessary to locate equipment within 10'-0" from edge of roof, provide railings. or… • means of securing fall protection devices with appropriate signage. | Washington Group (Rick Callor) Haskell (David Engdahl)
1735 | Fumes from equipment that contain toxic gases such as some refrigerants. | Mechanical | Mechanical | Design | Safety | Toxic substances (respiratory system damage or asphyxiation) | • Specify posting of MSDS's for all gaseous chemicals used as part of building maintenance. Specify a safety ventilation system to initiate automatically and alarm. • Where appropriate, specify and show locations for breathing apparatus. | Washington Group (Rick Callor) Haskell (David Engdahl)
1736 | Respiratory system damage resulting from off-gassing of chemical such as volatile organic compounds from caulks and adhesives. | Mechanical | Mechanical | Design | Safety | Toxic substances | • Where appropriate, specify an alternative non-off-gassing material. • Where off-gassing materials will be introduced regularly by users, specify enhanced filtration, local exhaust systems and IAQ sensors that alarm and/or increase ventilation. • Build-up of chemicals can occur in recently constructed buildings where materials are new and at the peak of off-gassing. Specify that the HVAC system will be run at the highest acceptable outside air rate during weekends for the first month or two of building operation. • Specify in the sequence of operation that HVAC systems to start up a few hours before anticipated occupancy, particularly after long periods of the system being off. For example, instead of starting systems at 6:00 a.m. on Monday morning, start them at 4:00 a.m. | Washington Group (Rick Callor) Haskell (David Engdahl)
1737 | Scalding from domestic hot water. | Mechanical | Mechanical | Design | Safety | Fire (burns) | Design for the lowest practical delivery temperature of hot water to fixtures, particularly to fixtures used by children, elderly, or medical patients. | Washington Group (Rick Callor) Haskell (David Engdahl)
1738 | Burned from hot relief or exhaust discharge. | Mechanical | Mechanical | Design | Safety | Fire (burns) | Locate relief from steam pressure reducing stations and emergency generator exhaust away from areas where maintenance will occur. | Washington Group (Rick Callor) Haskell (David Engdahl)
1739 | Fall into or through mechanical equipment floor or roof opening. | Mechanical | Mechanical | Design | Safety | Fall | • Avoid locating openings in public areas. • Provide protective grate to support weight of person over opening. | Washington Group (Rick Callor) Haskell (David Engdahl)
1740 | Slipping on wet floor such as in mechanical room | Mechanical | Mechanical | Design | Safety | Fall (slipping) | • Provide floor drains in floors subject to fluids such as mechanical rooms or maintenance areas. Locate drains next to fluid handling equipment such as pumps to collect fluid leaks and water discharged during repair/maintenance. • Pipe equipment drains to floor drain (avoid tripping hazard). | Washington Group (Rick Callor) Haskell (David Engdahl)
1741 | Slips/Falls | Civil | Structural - building usage | Design | Safety | Exposed concrete floor finish in wet areas could pose slip/fall hazard | Provide a light broom finish on all exposed to weather surfaces | Washington Group (Rick Callor) Haskell (David Engdahl)
1742 | Slips/Falls | Civil | Structural - building usage | Design | Safety | Inadequate edge protection could cause maintenance workers falling off roofs | Provide adequate railing or other means of fall protection along exposed perimeter of the building | Washington Group (Rick Callor) Haskell (David Engdahl)
1743 | Slips/Falls | Civil | Structural - building usage | Design | Safety | Wet stairs or extremely smooth stair tread surfaces could pose slip/fall hazard | Provide broom finish on all exposed concrete stair surfaces | Washington Group (Rick Callor) Haskell (David Engdahl)
1744 | Slips/Falls | Civil | Structural - building usage | Design | Safety | Unmarked steps in top of slab elevations could pose slip/fall hazard | In all locations where a slab depression is to remain, some warning marking, color transition or other design feature should be included to make it obvious to the user that the slab step occurs, slip resistant tread, adequate lighting | Washington Group (Rick Callor) Haskell (David Engdahl)
1745 | Slips/Falls | Civil | Structural - building usage | Design | Safety | Roof top screen wall can have diagonal steel tripping hazards and be too close to the units to safely walk around | Paint kicker posts in warning colors, provide a minimum of 3 foot clear between the equipment/walkways to screen walls. | Washington Group (Rick Callor) Haskell (David Engdahl)
1746 | Falls From Elevation | Civil | Structural - building usage | Design | Safety | Inadequate or no detailing to support window washing rigging could lead to window washer falls. | Provide a minimum eye hook and hold down point on all roofs, operable windows for cleaning from inside (creates large load on mechanical system), access path for cherry pickers. | Washington Group (Rick Callor) Haskell (David Engdahl)
1747 | Falls From Elevation | Civil | Structural - building usage | Design | Safety | Inadequate detailing or design of handrails and guards could lead to railing failure | Contact architects during design phase to assist in design of handrail and guard elements. | Washington Group (Rick Callor) Haskell (David Engdahl)
1748 | Falls from elevation | Civil | Structural - building usage | Design | Safety | Someone falling through a skylight opening could be seriously hurt. | Provide re-bars in skylight frame to avoid fall if skylight should break. | Washington Group (Rick Callor) Haskell (David Engdahl)
1749 | Fire | Civil | Structural - building usage | Design | Safety | Inadequate or incomplete fireproofing installation could cause premature building failure or weakening during a fire | Provide strict code compliance regarding material thickness' and fireproofing requirements | Washington Group (Rick Callor) Haskell (David Engdahl)
1750 | Terrorist activity | Civil | Structural - building usage | Design | Safety | Exploding bomb may cause significant portion of the building structure to collapse | 1. Increase the column strength beyond code minimums to withstand certain level blast 2. Add additional perimeter columns at mid bay for lowest two levels to provide additional level of bomb protection 3. Design perimeter beam to span double bay in case bomb explosion hits interior column 4. Review structural design to insure that measures against progressive collapse have been incorporated 5. Provide setbacks which preclude uncontrolled vehicular access to perimeter of the building | Washington Group (Rick Callor) Haskell (David Engdahl)
1751 | Personal safety/security | Civil | Structural - building usage | Design | Safety | Columns and walls improperly located or located in areas with low lighting levels provide intruder hiding locations | To the greatest extent possible minimize column size and quantity of solid walls in parking structures. Floor system also affects effectiveness of lighting. Double tee joists are less effective in "throwing" light. | Washington Group (Rick Callor) Haskell (David Engdahl)
1752 | Vehicular Safety | Civil | Structural - building usage | Design | Safety | Finish on traffic topping and waterproofing could pose automobile skidding hazard | Insure that specified traffic topping and waterproofing have skid resistant aggregates or are appropriate for reducing skids. | Washington Group (Rick Callor) Haskell (David Engdahl)
1753 | Vehicular Safety | Civil | Structural - building usage | Design | Safety | Columns in parking garages can be hit by vehicles | Use round columns in parking garages where columns impinge into the spaces to reduce potential for cars to hit | Washington Group (Rick Callor) Haskell (David Engdahl)
1754 | Vehicular Safety | Civil | Structural - building usage | Design | Safety | Columns in warehouses can be damaged by forktrucks | Provide bollards or concrete piers at base | Washington Group (Rick Callor) Haskell (David Engdahl)
1755 | Falling debris | Civil | Structural - building usage | Design | Safety | Items hard connected across expansion joints make break during building movement | Avoid hard connections across expansion joints | Washington Group (Rick Callor) Haskell (David Engdahl)
1756 | Floor Overloading | Civil | Structural - building usage | Design | Safety | Using small rooms and other building areas for heavy storage different than assumed during design can cause floor systems to become overloaded. | Install placards on all “undefined” potential storage room walls which indicate the design live load of that space. Install floor markings in areas which are not intended for heavy storage use. Design all “undefined spaces” for heavy storage live loads. | Washington Group (Rick Callor) Haskell (David Engdahl)
1757 | Roof joist overloading | Civil | Structural - building usage | Design | Safety | Roof not properly designed for mechanical equipment, conveying, cable tray loads | Coordinate all below roof equipment with A, M, E, P disciplines | Washington Group (Rick Callor) Haskell (David Engdahl)
1758 | Struck By -Structure Erection | Civil | Structural - construction | Construction | Safety | Column instability during erection if only two anchor bolt pattern is installed | Provide 4 bolt connections for all columns to foundations | Washington Group (Rick Callor) Haskell (David Engdahl)
1759 | Struck By - Structure Erection | Civil | Structural - construction | Construction | Safety | Column splice detail with connection only to the web | Provide flange to flange splice connection for typical detail | Washington Group (Rick Callor) Haskell (David Engdahl)
1760 | Struck By - Structure Erection | Civil | Structural - construction | Construction | Safety | Joist framing (applies to wood and cold formed metal framing) could collapse if not properly braced and anchored | Provide erection bridging to meet OSHA requirements | Washington Group (Rick Callor) Haskell (David Engdahl)
1761 | Falls From Elevation | Civil | Structural - construction | Construction | Safety | Slab openings/edges provide potential for workers to fall through | Provide requisite guardrails and toe boards at all slab openings/edges | Washington Group (Rick Callor) Haskell (David Engdahl)
1762 | Slips/Fall | Civil | Structural - construction | Construction | Safety | Slab depressions could cause tripping of construction worker | Provide removable yellow/black safety warning tape along all steps in floor slab, rope off area at steps, provide temporary construction ramp | Washington Group (Rick Callor) Haskell (David Engdahl)
1763 | Slips/Fall | Civil | Structural - construction | Construction | Safety | Deformed anchor bars (DBA's) which are shop applied to perimeter angles pose tripping and erection hazard | DBA's should be field attached after the decking is installed. | Washington Group (Rick Callor) Haskell (David Engdahl)
1764 | Slips/Fall | Civil | Structural - construction | Construction | Safety | Reinforcing bar placement for slabs and foundations could cause tripping of construction worker | Provide bar spacing less than 6 inches or greater than 16 inches to provide bars close enough to stand on and support weight or far enough apart to provide adequate room to step between bars. | Washington Group (Rick Callor) Haskell (David Engdahl)
1765 | Falls From Elevation | Civil | Structural - construction | Construction | Safety | Steel structures slab edges provide location where construction worker could fall | All steel columns should have a hole in which to install guardrails and lifelines at 21 and 42 inches above each floor | Washington Group (Rick Callor) Haskell (David Engdahl)
1766 | Falls From Elevation | Civil | Structural - construction | Construction | Safety | Steel deck could shift or lift off due to wind if not anchored immediately | Add specification requirements to require temporary anchoring of decking within one hour of placing | Washington Group (Rick Callor) Haskell (David Engdahl)
1767 | Falls From Elevation | Civil | Structural - construction | Construction | Safety | Poorly compacted soil may not be adequate to support temporary structures such as scaffolding | Provide notes on lowest level plans to require adequate soil compaction when scaffolding is soil supported. | Washington Group (Rick Callor) Haskell (David Engdahl)
1768 | Placement error | Civil | Structural - construction | Construction | Safety | Reinforcing bars not properly located in slabs and walls can have dramatic effect on load capacity of the structure | Provide uniformity in the reinforcing specified to simplify the different types of reinforcing bars layouts to ease placement and potential for mistakes | Washington Group (Rick Callor) Haskell (David Engdahl)
1769 | Impalement | Civil | Structural - construction | Construction | Safety | Construction workers who fall off formwork, could impale themselves on exposed reinforcing bars | Provide a 180 degree hook or impaling cap on the end of all wall reinforcing bars | Washington Group (Rick Callor) Haskell (David Engdahl)
1770 | Impalement | Civil | Structural - construction | Construction | Safety | Post-tension cables can injure other workers if jack fitting or cable fails during tensioning | Align post tension cables such that they are not directed towards the active work areas. | Washington Group (Rick Callor) Haskell (David Engdahl)
1771 | Electrocution | Civil | Structural - construction | Construction | Safety | Inadequate grounding of the structural steel could lead to electrocution of erectors | Provide grounding of structural steel beginning from foundation construction | Washington Group (Rick Callor) Haskell (David Engdahl)
1772 | Explosion | Civil | Structural - construction | Construction | Safety | Construction worker/testing agent in drilled shafts could inhale fumes or have possible explosion if fuel smells are present | Do not test shaft bearing capacity in presence of fuel odor, provide adequate ventilation first | Washington Group (Rick Callor) Haskell (David Engdahl)
1773 | Collapse | Civil | Structural - construction | Construction | Safety | Over excavation for structure undermines footings of adjacent structure | Insure underpinning of existing building foundation is adequate to avoid existing foundation blow-out. | Washington Group (Rick Callor) Haskell (David Engdahl)
1774 | Collapse/Structure damage | Civil | Structural - construction | Construction | Safety | Heavy Construction loads (such as pallets of masonry) can cause structure damage and possibly collapse if not accounted for | Work with project directors and managers to determine areas where temporary heavy construction loads may occur and insure structure has been designed to accommodate those loads. | Washington Group (Rick Callor) Haskell (David Engdahl)
1775 | Site excavation soils | Civil | Site | Design | Safety | Cave-ins | • Assess soil type and caution for potential of cave-ins. • For projects adjacent to open rock slopes, require rock fences to be erected or regularly spaced benches to be cut into the slopes to smother any falling rocks. | Washington Group (Rick Callor) Haskell (David Engdahl)
1776 | Blind intersections | Civil | Site | Design | Safety | Vehicular and pedestrian collisions | • Keep view triangle (20') clear of berms, landscaping, signage, screen walls, parking and equipment. | Washington Group (Rick Callor) Haskell (David Engdahl)
1777 | Auto and truck safety | Civil | Site | Design | Safety | Collisions | • Separate traffic. Avoid complex traffic patterns. • Use thermoplastic markings or buttons rather than paint for pavement markings. | Washington Group (Rick Callor) Haskell (David Engdahl)
1778 | Vehicular security barriers | Civil | Site | Design | Safety | Terrorist attacks | • For public or other buildings particularly vulnerable to terrorist attack, provide substantial vehicle limiting barriers at building. | Washington Group (Rick Callor) Haskell (David Engdahl)
1779 | Soft roadway shoulders | Civil | Site | Design | Safety | Equipment overturning | • Design roadway edges with shoulders to support weight of construction equipment. | Washington Group (Rick Callor) Haskell (David Engdahl)
1780 | Building entrances | Civil | Site | Design | Safety | Slips/Falls | • Locate exterior walkways and platforms away from the north side of the structure to prevent the buildup of moss and ice due to lack of sun. • Provide minimum slope across exterior walkways and platforms to prevent puddles. • Provide a non-slip walking surface on walkways and platforms adjacent to open water or exposed to the weather. • Do not have unanticipated, random steps along walkways. | Washington Group (Rick Callor) Haskell (David Engdahl)
1781 | Playground surfacing | Civil | Site | Design | Safety | Falls from elevation | • Provide grade surfaces at playground areas. | Washington Group (Rick Callor) Haskell (David Engdahl)
1782 | Existing utility lines | Civil | Site | Design | Safety | Electrocution, soil contamination | • Provide name, address and telephone numbers of local utility companies on drawings. • Provide location of shut-off valves. • Require hand excavation around existing underground utilities. | Washington Group (Rick Callor) Haskell (David Engdahl)
1783 | Utility lines | Civil | Site | Design | Safety | Cave-ins | • Require contractor to "pothole" for unknown underground utilities prior to excavation operations. • Design underground utilities to be placed using trenchless technologies. • Locate underground utilities and other below-grade features in areas easily accessible for excavation. Allow sufficient area around excavation for stockpiling the soil. • Require warning tape to be placed 12" above underground utility lines. | Washington Group (Rick Callor) Haskell (David Engdahl)
1784 | Manholes | Civil | Site | Design | Safety | Asphyxiation - confined space | • Provide safety warning signs at manhole. • Use grated manhole covers. | Washington Group (Rick Callor) Haskell (David Engdahl)
1785 | Steep slopes and embankments | Civil | Site | Design | Safety | Vehicular and pedestrian falling | • Avoid steep slopes. If unavoidable, provide protective rails and barriers. • Orient the project site or grade the site to minimize the amount of work on steep slopes. | Washington Group (Rick Callor) Haskell (David Engdahl)
1786 | Retaining walls (General) | Civil | Site | Design | Safety | Falls from elevation | • Provide guardrails at grade differentials greater than 30". | Washington Group (Rick Callor) Haskell (David Engdahl)
1787 | Retaining walls (Educational) | Civil | Site | Design | Safety | Falls from elevation | • Provide a 12" vertical barrier at grade differentials between 6" - 18". • Provide guardrails at grade differentials greater than 18". | Washington Group (Rick Callor) Haskell (David Engdahl)
1788 | Stormwater ponds, bodies of water, inlets | Civil | Site | Design | Safety | Drowning | • Design dry ponds. • Limit depth. • Provide childproof fencing or protective railings. • Provide protective grating at potentially fast flowing inlets and piping. | Washington Group (Rick Callor) Haskell (David Engdahl)
1789 | Maintenance of traffic | Civil | Site | Design | Safety | Demolition hazard, vehicular and pedestrian collisions | • Slow down ongoing public traffic as much as possible by using signage, flag people or by closing adjacent traffic lanes. • Minimize public access through or adjacent to the project site. Detour public traffic around project site. • Allow for pedestrian traffic to be isolated from construction vehicular traffic. | Washington Group (Rick Callor) Haskell (David Engdahl)
1790 | Landscaping/ overhead power line conflicts | Civil | Site | Design | Safety | Electrocution | • Avoid potentially tall landscape materials near overhead power lines. | Washington Group (Rick Callor) Haskell (David Engdahl)